SECTION 260553 - IDENTIFICATIONS

- GENERAL

  - Equipment, disconnect switches, motor starters, pushbutton stations, special device plates, and similar materials shall be clearly marked as to their function and use.  Markings shall be applied neatly and conspicuously to the front of each item of equipment with 1/2" white lamacoid plate (or equivalent) with black letters 1/4" high.

  - The Contractor shall provide clearly legible typewritten directories in each electrical panel indicating the area, item of equipment, etc., controlled by each switch, breaker, fuse, etc.  These directories are to be inserted into plastic card holders in each panel.  The Contractor shall be required to demonstrate the accuracy of the panel directory for a random sampling of circuits in each panelboard as directed in the field by the Engineer with corrections made immediately so it is imperative that care be taken during installation to insure 100% accurate directories.

  - Branch circuit panelboards and switch gear shall be provided with a black lamacoid plastic plate with 1/2" black letters.  Branch circuit switches shall be designated as to function.  Panelboard and switchgear labels shall indicate the source they are fed from, and the circuit number at that source.   Panelboards shall also indicate color coding of the branch circuit phase conductors supplied.  Clearly indicate the exact label legend to be furnished with each panelboard and switchgear on the shop drawings for each item of equipment prior to submission of shop drawings.

EXAMPLE:

PANEL “XYZ” FED FROM “MDP – 2”

  - Where branch circuit panelboards and switchgear are connected to an emergency source, the lamacoid plate shall be red, and the word "emergency" shall be incorporated into the legend.  In healthcare applications, the NEC – designated branch (life safety, critical or equipment branch) shall also be incorporated into the legend, all in ¼” letters.  Also provide similar plates and legends for automatic transfer switches, and equipment disconnects 100 amps and larger.

  - Lamacoid plates shall be located at center of top of trim for branch circuit panels, switch gear, and centered at side for branch circuit switches.  Fasten with self-tapping stainless steel screws or other approved method.

END OF IDENTIFICATIONS