SECTION 260573 - ELECTRICAL SYSTEM STUDIES

# GENERAL

## RELATED DOCUMENTS

### Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

## SUMMARY

### This Section includes computer-based, fault-current and arc flash studies.

### Product Data:  For computer software program to be used for studies.

### Qualification Data:  For coordination-study specialist.

### Other Action Submittals:  The following submittals shall be made after the approval process for system protective devices has been completed.  Submittals shall be in digital form.

#### Study input data, including completed computer program input data sheets.

#### Study and Equipment Evaluation Reports.

#### Coordination-Study Report.

#### Arc Flash Labeling Report.

## QUALITY ASSURANCE

### Studies shall use computer programs that are distributed nationally and are in wide use.  Software algorithms shall comply with requirements of standards and guides specified in this Section.  Manual calculations are not acceptable.

### Coordination-Study Specialist Qualifications:  An entity experienced in the application of computer software used for studies, having performed successful studies of similar magnitude on electrical distribution systems using similar devices.

#### Professional engineer, licensed in the state where Project is located, shall be responsible for the study.  All elements of the study shall be performed under the direct supervision and control of engineer.

### Comply with IEEE 242 for short-circuit currents and coordination time intervals.

### Comply with IEEE 399 for general study procedures.

# PRODUCTS

## COMPUTER SOFTWARE DEVELOPERS

### Computer Software Developers: Subject to compliance with requirements, provide products by one of the following:

#### CGI CYME.

#### EDSA Micro Corporation.

#### ESA Inc.

#### Operation Technology, Inc.

#### SKM Systems Analysis, Inc.

## COMPUTER SOFTWARE PROGRAM REQUIREMENTS

### Comply with IEEE 399.

### Analytical features of fault-current-study computer software program shall include "mandatory," "very desirable," and "desirable" features as listed in IEEE 399.

### Computer software program shall be capable of plotting and diagramming time-current-characteristic curves as part of its output.  Computer software program shall report device settings and ratings of all overcurrent protective devices and shall demonstrate selective coordination by computer-generated, time-current coordination plots.

# EXECUTION

## EXAMINATION

### Examine Project overcurrent protective device submittals for compliance with electrical distribution system coordination requirements and other conditions affecting performance.  Devices to be coordinated are indicated on Drawings.

## POWER SYSTEM DATA

### Gather and tabulate the following input data to support coordination study:

#### Product Data for overcurrent protective devices specified in other Division 26 Sections and involved in overcurrent protective device coordination studies.  Use equipment designation tags that are consistent with electrical distribution system diagrams, overcurrent protective device submittals, input and output data, and recommended device settings.

#### Impedance of utility service entrance.

#### Electrical Distribution System Diagram:  In hard-copy and electronic-copy formats, showing the following:

##### Circuit-breaker and fuse-current ratings and types.

##### Relays and associated power and current transformer ratings and ratios.

##### Transformer kilovolt amperes, primary and secondary voltages, connection type, impedance, and X/R ratios.

##### Generator kilovolt amperes, size, voltage, and source impedance.

##### Cables:  Indicate conduit material, sizes of conductors, conductor material, insulation, and length.

##### Busway ampacity and impedance.

##### Motor horsepower and code letter designation according to NEMA MG 1.

#### Data sheets to supplement electrical distribution system diagram, cross-referenced with tag numbers on diagram, showing the following:

##### Transformer characteristics, including primary protective device, magnetic inrush current, and overload capability.

##### Motor full-load current, locked rotor current, service factor, starting time, type of start, and thermal-damage curve.

##### Generator thermal-damage curve.

##### Manufacturer, frame size, interrupting rating in amperes rms symmetrical, ampere or current sensor rating, long-time adjustment range, short-time adjustment range, and instantaneous adjustment range for circuit breakers.

##### Panelboards, switchboards, motor-control center ampacity, and interrupting rating in amperes rms symmetrical.

## FAULT-CURRENT STUDY

### Calculate the maximum available short-circuit current in amperes rms symmetrical at circuit-breaker positions of the electrical power distribution system.  The calculation shall be for a current immediately after initiation and for a three-phase bolted short circuit at each of the following:

#### Switchgear and switchboard bus

#### Medium-voltage switch and transformers

#### Distribution panelboard

#### Branch circuit panelboard

### Study electrical distribution system from normal and alternate power sources throughout electrical distribution system for Project.  Include studies of system-switching configurations and alternate operations that could result in maximum fault conditions.

### Calculate momentary and interrupting duties on the basis of maximum available fault current.

### Calculations to verify interrupting ratings of overcurrent protective devices shall comply with IEEE 241 and IEEE 242.

#### Transformers:

##### ANSI C57.12.10

##### ANSI C57.12.22

##### ANSI C57.12.40

##### IEEE C57.12.00

##### IEEE C57.96

#### Low-Voltage Circuit Breakers:  IEEE 1015 and IEEE C37.20.1.

#### Low-Voltage Fuses:  IEEE C37.46.

### Study Report:

#### Show calculated X/R ratios and equipment interrupting rating (1/2-cycle) fault currents on electrical distribution system diagram.

### Equipment Evaluation Report:

#### For 600-V overcurrent protective devices, ensure that interrupting ratings are equal to or higher than calculated 1/2-cycle symmetrical fault current.

#### For devices and equipment rated for asymmetrical fault current, apply multiplication factors listed in the standards to 1/2-cycle symmetrical fault current.

#### Verify adequacy of phase conductors at maximum three-phase bolted fault currents; verify adequacy of equipment grounding conductors and grounding electrode conductors at maximum ground-fault currents.  Ensure that short-circuit withstand ratings are equal to or higher than calculated 1/2-cycle symmetrical fault current.

## ARC FLASH HAZARD ANALYSIS

### The arc flash hazard analysis shall be performed according to the IEEE 1584 equations that are presented in NFPA70E-2004, Annex D.

### The flash protection boundary and the incident energy shall be calculated at all significant locations in the electrical distribution system.  This includes all switchboards, switchgear, motor-control centers, panelboards, busway and splitters.

### Safe working distances shall be based upon the calculated arc flash boundary considering an incident energy of 1.2 cal/cm2.

### When appropriate, the short circuit calculations and the clearing times of the phase overcurrent devices will be retrieved from the short-circuit and coordination study model. Ground overcurrent relays should not taken into consideration when determining the clearing time when performing incident energy calculations.

### The short-circuit calculations and the corresponding incident energy calculations for multiple system scenarios must be compared and the greatest incident energy must be uniquely reported for each equipment locations.  Calculations must be performed to represent the maximum and minimum contributions of fault current magnitude for all normal and emergency operating conditions.  The minimum calculation will assume that the utility contribution is at a minimum and will assume a minimum motor contribution (all motors off).  Conversely, the maximum calculation will assume a maximum contribution from the utility and will assume the maximum amount of motors to be operating.  Calculations shall take into consideration the parallel operation of synchronous generators with the electric utility, where applicable.

### The incident energy calculations must consider the accumulation of energy over time when performing arc flash calculations on buses with multiple sources.  Iterative calculations must take into account the changing current contributions, as the sources are interrupted or decremented with time.  Fault contribution from motors and generators should be decremented as follows:

#### Fault contribution from induction motors should not be considered beyond 3-5 cycles.

#### Fault contribution from synchronous motors and generators should be decayed to match the actual decrement of each as closely as possible (e.g. contributions from permanent magnet generators will typically decay from 10 per unit to 3 per unit after 10 cycles).

### For each equipment location with a separately enclosed main device (where there is adequate separation between the line side terminals of the main protective device and the work location), calculations for incident energy and flash protection boundary shall include both the line and load side of the main breaker.

### When performing incident energy calculations on the line side of a main breaker (as required per above), the line side and load side contributions must be included in the fault calculation.

### Mis-coordination should be checked amongst all devices within the branch containing the immediate protective device upstream of the calculation location and the calculation should utilize the fastest device to compute the incident energy for the corresponding location.

### Arc Flash calculations shall be based on actual overcurrent protective device clearing time.  Maximum clearing time will be capped at 2 seconds based on IEEE 1584-2002 section B.1.2.  Where it is not physically possible to move outside of the flash protection boundary in less than 2 seconds during an arc flash event, a maximum clearing time based on the specific location shall be utilized.

### Incident energy and flash protection boundary calculations

#### Arcing fault magnitude

#### Protective device clearing time

#### Duration of arc

#### Arc flash boundary

#### Working distance

#### Incident energy

#### Hazard Risk Category

#### Recommendation for arc flash energy reduction

## ARC FLASH WARNING LABELS

### The contractor of the Arc Flash Hazard Analysis shall provide a 3.5 in. x 5 in. thermal transfer type label of high adhesion polyester for each work location analyzed.

### After labels will be based on recommended overcurrent device settings and will be provided after the results of the analysis have been presented to the owner and after any system changes, upgrades or modifications have been incorporated in the system.

### The label shall include the following information, at a minimum:

#### Location designation

#### Nominal voltage

#### Flash protection boundary

#### Hazard risk category

#### Incident energy

#### Working distance

#### Engineering report number, revision number and issue date.

### Labels shall be machine printed, with no field markings.

### Arc flash labels shall be provided in the following manner and all labels shall be based on recommended overcurrent device settings.

#### For each 600, 480 and applicable 208 volt panelboard, one arc flash label shall be provided.

#### For each motor control center, one arc flash label shall be provided.

#### For each low voltage switchboard, one arc flash label shall be provided.

#### For each switchgear, one flash label shall be provided.

#### For medium voltage switches, one arc flash label shall be provided.

### END OF ELECTRICAL SYSTEM STUDIES