SECTION 260544 - EXCAVATION, TRENCHING, BACKFILLING AND GRADING

- GENERAL

  - Each Contractor's attention is directed to Section 260501, General Provisions, Electrical and all other contract documents as they may apply to his work.  Division 03, 31 an3 33 shall apply to work by all contractors.

  - Each Contractor shall include all excavating, filling, grading and related items required to complete his work as shown on the drawings and specified herein.

  - Electrical distribution lines and underground telephone or TV cables shall, in no case, be placed in the same trench with sanitary, storm, domestic or fire protection water lines.  Phone cable may, at the Contractor's option, and if acceptable to both utility companies, be placed in a common trench with power lines as long as 8" of earth separation is maintained.  T.V. cable shall, in all cases, be placed in a separate trench with two feet separation from electrical power lines.

  - Minimum depths of bury shall be as indicated on the drawings or required by code, whichever is greater.

- SUBSURFACE DATA

  - Materials to be excavated shall be unclassified, and shall include earth, rock, or any other material encountered in the excavation to the depth and extent indicated on the drawings and specified herein.  No adjustment in the Contract sum will be made on account of the presence or absence of rock, shale, or other materials encountered in the excavating.

- BENCH MARKS AND MONUMENTS

  - Maintain carefully all bench marks, monuments and other referenced points. If disturbed or destroyed, replace as directed.

- EXCAVATION

  - Each Contractor shall accept the site as he finds it and remove all trash, rubbish and material from the site prior to starting excavation for his work.

  - Excavate trenches to sufficient width and depth for proper installation of the work and where required, smooth the bottom on the trench with hand tools.

  - The removal of rock shall be accomplished by use of hand or power tools only.  Blasting shall not be permitted unless authorized in writing by the Architect.  Any damage to existing structures, exterior services or rock intended for bearing, shall be corrected at the responsible Contractor's expense.

  - Keep trenches free from water while construction therein is in progress. Under no circumstances lay conduit or cable in water. Pumping or bailing water from this Contractor's trenches, which is required during construction shall be accomplished at his expense.

  - In no case shall excavation work be accomplished that will damage in any way the new structure, existing structures, equipment, etc.  Each Contractor shall take the necessary steps to prevent flow of eroded earth by water or landslide onto the property of others, or against the structures.  The repair of all such damage, or any other damage incurred in the course of excavation, shall be borne by the responsible Contractor.

- BACKFILL

  - Backfill shall be accomplished with clean debris free earth and the new earth tamped at 12" intervals so as to avoid earth sinks along the trench.  The responsible Contractor will be required to return to the project and fill any sunken areas along the route of his work.

  - Backfill trenches only after conduit and cable have been inspected, tested, and locations of pipe lines have been recorded on "as-built" drawings.

  - The backfill below paved areas shall be brought to proper grade to receive the sub-base and paving.  No paving shall be placed on uncompacted fill.

  - The backfill below sodded or seeded areas shall be brought to within six inches of finished grade.  The remaining six inches shall be backfilled with clean soil.

END OF EXCAVATION