Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 270610 – CATY DISTRIBUTION SYSTEM

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - The Contractor is directed to examine each and every section of these specifications, all drawings relating to the Contract Documents, any and all Addenda, etc., for work described elsewhere that may relate to the provision of the work described herein.  Materials and performance requirements are specified elsewhere herein that relate to these systems.

        - All layout and installation of communications infrastructure shall be in accordance with ANSI / TIA 568 and the BICSI TDMM.

      - SUMMARY

        - Section Includes:

          - Pathways.

          - UTP cabling.

          - Optical Fiber cabling.

          - Cable connecting hardware, patch panels, and cross-connects.

          - Telecommunications outlet/connectors.

          - Cabling system identification products.

          - Cable management system.

        - The Contractor shall furnish all materials, labor, services, purchasing, testing of completely installed systems, etc., that are indicated or required to provide a complete telecommunications distribution network for the project.

        - The telecommunications distribution network shall be designed and installed in a format and construction as required for an IEEE 802.3ae compliant 1Gb Ethernet system.  It shall be physically wired in a star configuration.

        - The telecommunications distribution system shall be installed complete, except as hereinafter described.  The system shall be provided with all wall plates, inserts, wiring, equipment racks and supports, copper and fiber termination equipment, connections, wire terminations and identifications, 120 VAC power outlets, grounding etc., for a completely functioning premises wiring network.  Components of each subsystem shall be of one manufacture, and be tested and certified as compatible to provide the specified performance.

        - The system active electronic hardware and software shall be installed by the Owner or his vendor, unless otherwise noted or specified.

      - BACKBONE CABLING DESCRIPTION

        - Backbone cabling system shall provide interconnections between communications equipment rooms, main terminal space, and entrance facilities in the telecommunications cabling system structure.  Cabling system consists of backbone cables, intermediate and main cross-connects, mechanical terminations, and patch cords or jumpers used for backbone-to-backbone cross-connection.

        - Backbone cabling cross-connects may be located in communications equipment rooms or at entrance facilities.  Bridged taps and splitters shall not be used as part of backbone cabling.

        - Backbone cabling system shall comply with transmission standards in ANSI/TIA-568-C.1, when tested according to test procedures of this standard.

      - HORIZONTAL CABLING DESCRIPTION

        - Horizontal cable and its connecting hardware provide the means of transporting signals between the telecommunications outlet/connector and the horizontal cross-connect located in the communications equipment room.  This cabling and its connecting hardware are called "permanent link," a term that is used in the testing protocols.  Splices shall not be installed in the horizontal cabling.

        - The maximum allowable horizontal cable length is 275 feet.

        - Horizontal cabling system shall comply with transmission standards in ANSI/TIA-568-C.1, when tested according to test procedures of this standard.

      - SUBMITTALS

First two paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

        - Product Data:  For each type of product indicated.

Retain subparagraph below for coaxial cable.  Installation data for UTP and optical fiber cabling are specified in referenced TIA/EIA standards.  See Editing Instruction No. 5 in the Evaluations for discussion about recommended parameters.

          - Submittals shall also be accompanied by a detailed bill of material, including part numbers and quantities.

        - Shop Drawings:

Retain one of first two subparagraphs below.

          - System Labeling Schedules:  Electronic copy of labeling schedules, in software and format selected by Owner.

          - Cabling administration drawings and printouts.

          - Wiring diagrams to show typical wiring schematics including the following:

            - Cross-connects.

            - Patch panels.

            - Patch cords.

          - Cross-connects and patch panels.  Detail mounting assemblies, and show elevations and physical relationship between the installed components.

          - Cable tray layout, showing cable tray route to scale, with relationship between the tray and adjacent structural, electrical, and mechanical elements.  Include the following:

            - Vertical and horizontal offsets and transitions.

            - Clearances for access above and to side of cable trays.

            - Vertical elevation of cable trays above the floor or bottom of ceiling structure.

            - Load calculations to show dead and live loads as not exceeding manufacturer's rating for tray and its support elements.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

        - Qualification Data:  For Installer, qualified layout technician, installation supervisor, and field inspector.

        - Source quality-control reports.

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

        - Maintenance Data:  For connectors to include in maintenance manuals.

Retain paragraph below for PC-based, cabling administration systems.

      - QUALITY ASSURANCE

BICSI is an industry trade association.  See Editing Instruction No. 2 in the Evaluations for summaries of qualifications for registration.

        - Installer Qualifications:  Cabling Installer must have personnel certified by the cable manufacturer or BICSI on staff.

Retain first paragraph below if Contractor or manufacturer selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.  Qualification requirements are in addition to those specified in Division 01 Section "Quality Requirements," which also includes the definition for "NRTL" (nationally recognized testing laboratory).

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - Telecommunications Pathways and Spaces:  Comply with NFPA 70, and TIA/EIA-569-A.

      - Grounding:  Comply with NFPA 70, and ANSI/TIA-607-B

      - DELIVERY, STORAGE, AND HANDLING

According to BICSI ITSIM, cables should be tested upon receipt.

        - Test cables upon receipt at Project site.

Retain one or both of first two subparagraphs below.

          - Test optical fiber cable to determine the continuity of the strand end to end.  Use optical fiber flashlight or optical loss test set.

          - Test each pair of UTP cable for open and short circuits.

      - COORDINATION

Revise this article to specify coordination with other parties involved in finalizing communications equipment room work.  See Editing Instruction No. 3 in the Evaluations.

        - Coordinate layout and installation of communications equipment with Owner's telecommunications and LAN equipment and service suppliers.

          - Meet jointly with telecommunications and LAN equipment suppliers, Engineer, and Owner to exchange information and agree on details of equipment arrangements and installation interfaces.

          - Record agreements reached in meetings and distribute them to other participants.

          - Adjust arrangements and locations of racks, sleeves, cross-connects, and patch panels in equipment rooms to accommodate and optimize arrangement and space requirements of telephone and LAN equipment.

        - Coordinate location of power raceways and receptacles with locations of communications equipment requiring electrical power to operate.

- PRODUCTS

      - PATHWAYS

        - General Requirements:  Comply with ANSI/TIA-569-C.

        - Cable Trays:

          - Comply with requirements in Division 26 Section “Raceways & Fittings”.

        - Conduit and Boxes:  Comply with requirements in Division 26 Sections "Raceways and Fittings” and “Cabinets, Outlet Boxes, and Pull Boxes”.

          - Outlet boxes shall be no smaller than 4" x 4" x 2 5/8"” with a double gang plaster ring and integral wire management.

          - Minimum conduit size is 1”.  Interior conduit shall be EMT or RGS.  Exterior conduit shall be Schedule 40 PVC.

          - All conduits shall be stubbed out from wall to an accessible point above ceiling or to the bottom of structure when no ceiling is to be installed.  Provide category-rated J-hook path to cable tray.

          - Provide all conduits with connector and plastic bushing at termination point.

      - BACKBOARDS

        - General Frame Requirements:

          - Distribution Frames:  Freestanding and wall-mounting, modular-steel units designed for telecommunications terminal support and coordinated with dimensions of units to be supported.

          - Module Dimension:  Width compatible with EIA 310 standard, 19-inch panel mounting.

          - Finish:  Manufacturer's standard, baked-polyester powder coat.

        - Floor-Mounted Racks:  Modular-type, steel construction.

          - Vertical and horizontal cable management channels, top and bottom cable troughs, grounding lug.

          - Baked-polyester powder coat finish.

          - Two-post racks shall be furnished with a 16 ¼” wide upright for extended equipment support.

        - Cable Management for Equipment Frames:

          - Metal, with integral wire retaining fingers.

          - Baked-polyester powder coat finish.

          - Vertical cable management panels shall have front and rear channels, with covers.  Provide vertical management on both sides of all racks.

          - Provide horizontal crossover cable manager at the top of each relay rack and between/below all patch panels, with a minimum height of two rack units each.

      - UTP BACKBONE CABLE

Copy this article and re-edit for each product.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

        - Description:  100-ohm, UTP, formed into 25-pair binder groups covered with a gray thermoplastic jacket.

          - Comply with ANSI/ICEA S-90-661 for mechanical properties.

          - Comply with TIA/-568-C.1 for performance specifications.

          - Comply with TIA/-568-C.2, Category 5.

          - Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 444 and NFPA 70 for the following types:

Type requirements in subparagraphs below are minimum requirements and may be revised to suit Project.  Retain options if "permitted substitutions," as defined in NFPA 70, are appropriate for this Project.

            - Communications, Riser Rated:  Type CMR or CMP complying with UL 1666.

        - All cable that enters or exits any building shall be provided with MOV protectors on each end.

      - UTP BACKBONE CABLE HARDWARE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

See Editing Instruction No. 4 in the Evaluations for discussion about 110-style IDC connectors and connector blocks.

        - General Requirements for Cable Connecting Hardware:  Comply with TIA/EIA-568-B.2, IDC type, with modules designed for punch-down caps or tools.  Cables shall be terminated with connecting hardware of same category or higher.

        - Connecting Blocks: 110-style IDC for Category 5.  Provide blocks for the number of cables terminated on the block, plus 25 percent spare.  Integral with connector bodies, including plugs and jacks where indicated.

Delete first paragraph below if cross-connection is accomplished exclusively on patch panels.

        - Cross-Connect:  Modular array of connecting blocks arranged to terminate building cables and permit interconnection between cables.

Coordinate subparagraph below with Drawings for quantity of fields.

        - Patch Panel:  Modular panels housing multiple-numbered jack units with IDC-type connectors at each jack for permanent termination of pair groups of installed cables.

Coordinate subparagraph below with Drawings for quantity of fields.

          - Number of Jacks per Field:  One for each four-pair UTP cable indicated plus spares and blank positions adequate to suit specified expansion criteria.

        - Jacks and Jack Assemblies:  Modular, color-coded, eight-position modular receptacle units with integral IDC-type terminals.

      - UTP HORIZONTAL CABLE

Copy this article and re-edit for each product.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

        - Description:  100-ohm, 4-pair Unshielded UTP, covered with a thermoplastic jacket.

          - Comply with ICEA S-90-661 for mechanical properties.

          - Comply with ANSI/TIA-568-C.1 for performance specifications.

          - Comply with ANSI/TIA-568-C.2 Category 6 up to 250 MHz.

          - Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 444 and NFPA 70 for the following types:

Type requirements in subparagraphs below are minimum requirements and may be revised to suit Project.  Retain options if "permitted substitutions," as defined in NFPA 70, are appropriate for this Project.

            - Communications, General Purpose:  Type CM or CMG.

            - Communications, Riser Rated:  Type CMR or CMP.

      - UTP CABLE HARDWARE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

See Editing Instruction No. 4 in the Evaluations for discussion about 110-style IDC connectors and connector blocks.

        - General Requirements for Cable Connecting Hardware:  Comply with ANSI/EIA-568-C.2, IDC type, with modules designed for punch-down caps or tools.  Cables shall be terminated with connecting hardware of same category or higher.

        - Connecting Blocks:  Shielded modular jack to be compatible with cabling system.  Provide blocks for the number of cables terminated on the block, plus 25 percent spare.  Integral with connector bodies, including plugs and jacks where indicated.

Delete first paragraph below if cross-connection is accomplished exclusively on patch panels.

        - Patch Panel:  Modular panels housing 24 or 48 modular snap-in jack units.

Coordinate subparagraph below with Drawings for quantity of fields.

          - Number of Jacks per Field:  One for each four-pair UTP cable indicated, plus spares and blank positions adequate to suit specified expansion criteria.

        - Jacks and Jack Assemblies:  Modular, color-coded, eight-position modular receptacle units with integral IDC-type terminals.

Cords are generally available in lengths to 20 feet (6 m) and longer in 24-inch (600-mm) increments.

        - Patch Cords:  Provide factory-made, four-pair Category 6 cables in 48-inch lengths; terminated with eight-position modular plug at each end.

Retain one of two subparagraphs below; retain first for Category 6, second for Category 5e patch cords.

          - Patch cords shall have bend-relief-compliant. Patch cords shall have latch guards to protect against snagging.

          - Provide quantity to match quantity of horizontal cables.

      - TELECOMMUNICATIONS OUTLET/CONNECTORS

        - Jacks:  100-ohm, unshielded balanced, twisted-pair connector; four-pair, eight-position modular.  Comply with ANSI/TIA-568-C.2 up to 250 MHz.

Coordinate paragraph below with other items specified to be mounted in workstation faceplates.  Revise paragraph if faceplate elevations are on Drawings.

        - Workstation Outlets:  Connector assemblies mounted in two gang faceplate.  Provide number of ports as shown on the Drawings.

Retain one of first two subparagraphs below, or retain both as required to match Division 26 Section "Wiring Devices."

          - Plastic Faceplate:  High-impact plastic.  Coordinate color with Division 26 Section "Wiring Devices and Plates."

          - For use with snap-in jacks accommodating any combination of UTP, optical fiber, and coaxial work area cords.

            - Flush mounting jacks, positioning the cord at a 45-degree angle.

Retain one of three subparagraphs below; retain first for metal faceplates.

          - Legend:  Snap-in, clear-label covers and machine-printed paper inserts.

      - OPTICAL FIBER CABLE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

        - Description:  Multimode, 50/125 micrometer, laser optimized, non-conductive, loose tube outside plant optical fiber cable.

Retain first subparagraph below for indoor cable.  ICEA standard for outside plant is ICEA S-87-640.

          - Comply with ICEA S-83-596 for mechanical properties.

          - Comply with TIA/EIA-568-C.3 for performance specifications.

Retain first option in first subparagraph below for 50/125-micrometer cable; retain second for 62.5/125-micrometer cable.

          - Comply with ANSI/TIA-492AAAA-B for detailed specifications.

          - Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 444, UL 1651, and NFPA 70.

Type requirements in first six subparagraphs below are minimum requirements and may need to be revised to suit Project.  OFC, OFCR, OFCG, and OFCP are conductive optical fiber cables that might have application in industrial settings.  Retain options if "permitted substitutions," as defined in NFPA 70, are appropriate for this Project.

Retain first subparagraph below even if nonconductive cable is specified above.  If both conductive and nonconductive cables are specified, indicate locations of each on Drawings.

          - Provide with central non-conductive strength member.

          - Minimum Effective Modal Bandwidth:  2000 MHz-km at 850 nm.

          - Individual fiber strands shall be color coded per telecommunications industry practice.

          - Number of strands shall be as noted on Drawings

          - Fiber strands shall meet the following specifications:

            - Fiber Type - Multi-mode, glass core, glass cladding.

            - Core Diameter - 50 microns +/- 3 microns.

            - Core/Clad Concentricity Error- < or = 3.0 microns.

            - Cladding diameter - 125 microns +/- 1 micron.

            - Cladding Noncircularity- < or = 1%.

            - Maximum attenuation at 850 nanometers (nominal) 3.0 dB/km.

            - Maximum attenuation at 1300 nanometers (nominal) 1.0 dB/km.

            - ISO/IEC 11801 Type: OM3.

        - Jacket:

          - Jacket Color:  Aqua.

          - Cable cordage jacket, fiber, unit, and group color shall be according to ANSI/TIA-598-C.

          - Imprinted with fiber count, fiber type, and aggregate length at regular intervals not to exceed 40 inches.

          - Hybrid single mode/multimode cable may be used subject to performance criteria above.

      - OPTICAL FIBER CABLE HARDWARE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

        - Cross-Connects and Patch Panels:  Modular panels housing multiple-numbered, duplex cable connectors.

Coordinate subparagraph below with Drawings for quantity of fields.

          - Number of Connectors per Field:  One for each fiber of cable or cables assigned to field, plus spares and blank positions adequate to suit specified expansion criteria.

        - Patch Cords:  Provide factory-made, dual-fiber cables in 36-inch (900-mm) lengths, quantity to match quantity of fibers.

        - Cable Connecting Hardware:

          - Comply with Optical Fiber Connector Intermateability Standards (FOCIS) specifications of TIA/EIA-604-2, TIA/EIA-604-3-A, and TIA/EIA-604-12.  Comply with ANSI/TIA-568-C.3.

Type SC is a subscriber connector and Type ST is a straight-tip, single-fiber connector; both are in common use.  Recently developed connectors are Type LC, which is an upgraded version of either Type SC or Type ST with a lower insertion loss, and Type MT-RJ, which is a no-epoxy, no-polish connector.

          - Quick-connect, simplex and duplex, Type SC.

      - SOURCE QUALITY CONTROL

Retain first paragraph below if required.  Independent certification may be acceptable to authorities having jurisdiction without further monitoring of plant's quality-control and testing program by Owner..

        - Factory test UTP and optical fiber cables on reels according to ANSI/TIA-568-C.1.

        - Factory test UTP cables according to ANSI/TIA-568-C.2.

See Division 01 Section "Quality Requirements" for retesting and reinspecting requirements and Division 01 Section "Execution" for requirements for correcting the Work.

        - Cable will be replaced by contractor if it does not pass tests listed above and inspections.

        - Prepare test and inspection reports.

      - GROUNDING

        - Comply with requirements in Division 26 Section "Grounding and Bonding” for grounding conductors and connectors.

        - Telecommunications Main Bus Bar:

          - Connectors:  Mechanical type, cast silicon bronze, solderless compression-type wire terminals, and long-barrel, two-bolt connection to ground bus bar.

          - Ground Bus Bar:  Copper, minimum 1/4 inch thick by 4 inches wide with 9/32-inch holes spaced 1-1/8 inches apart.

          - Stand-Off Insulators:  Comply with UL 891 for use in switchboards, 600 V.  Lexan or PVC, impulse tested at 5000 V.

        - Comply with ANSI -607-B.

      - LABELING

        - Comply with TIA/EIA-606-B and UL 969 for a system of labeling materials, including label stocks, laminating adhesives, and inks used by label printers.

- EXECUTION

      - ENTRANCE FACILITIES

        - Install buried entrance pathway complying with Division 26 Section "Raceway and Fittings”.

        - Comply with NECA 1.

        - Comply with BICSI TDMM for layout and installation of communications equipment rooms.

        - Bundle, lace, and train conductors and cables to terminal points without exceeding manufacturer's limitations on bending radii.  Install lacing bars and distribution spools.

      - WIRING METHODS

Retain one of first two paragraphs below and coordinate with Drawings.  Delete both if wiring methods for system are indicated on Drawings.

        - Wiring Method:  Install cables completely within raceways and cable trays. Conceal raceway except in unfinished spaces.

Retain first subparagraph below if retaining unenclosed wiring method option in paragraph above.

          - Comply with requirements for raceways and boxes specified in Division 26 Sections "Raceway and Fittings” and “Cabinets, Outlet Boxes, and Pull Boxes”.

        - Wiring within Enclosures:  Bundle, lace, and train cables within enclosures.  Connect to terminal points with no excess and without exceeding manufacturer's limitations on bending radii.  Provide and use lacing bars and distribution spools.

      - INSTALLATION OF PATHWAYS

        - Cable Trays:  Comply with NEMA VE 2 and ANSI/TIA-569-C.

Coordinate cable connection hardware installations and specialty arrangements with layout drawings and with requirements specified for communications equipment rooms.  If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Comply with ANSI/TIA-569-C for pull-box sizing and length of conduit and number of bends between pull points.

        - Install manufactured conduit sweeps and long-radius elbows whenever possible.

        - Pathway Installation in Communications Equipment Rooms:

          - Position conduit ends adjacent to a corner on backboard where a single piece of plywood is installed, or in the corner of room where multiple sheets of plywood are installed around perimeter walls of room.

          - Install cable trays complete around room as shown on drawings.  Install cable ladder directly on top of racks and connect to perimeter tray.

          - Secure conduits to backboard when entering room from overhead.

          - Extend conduits 4 inches above finished floor and/or 18” below ceiling structure.

          - Install metal conduits with grounding bushings and connect with grounding conductor to grounding bar.

        - Backboards:  Install backboards with 96-inch dimension vertical.  Butt adjacent sheets tightly, and form smooth gap-free corners and joints.  Provide on all walls.

      - INSTALLATION OF CABLES

        - Comply with NECA 1.

        - General Requirements for Cabling:

          - Comply with ANSI/TIA-568-C.1.

          - Comply with BICSI ITSIM, Ch. 6, "Cable Termination Practices."

          - Install 110-style IDC termination hardware for backbone cable and modular jacks for horizontal cable.

          - Terminate all conductors; no cable shall contain unterminated elements.  Make terminations only at indicated outlets, terminals, cross-connects, and patch panels.

          - Cables may not be spliced.

          - Install lacing bars to restrain cables, to prevent straining connections, and to prevent bending cables to smaller radii than minimums recommended by manufacturer.

          - Bundle, lace, and train conductors to terminal points without exceeding manufacturer's limitations on bending radii, but not less than radii specified in BICSI ITSIM, "Cabling Termination Practices" Chapter.  Use lacing bars and distribution spools.

          - Do not install bruised, kinked, scored, deformed, or abraded cable.  Do not splice cable between termination, tap, or junction points.  Remove and discard cable if damaged during installation and replace it with new cable.

          - Cold-Weather Installation:  Bring cable to room temperature before de-reeling.  Heat lamps shall not be used for heating.

          - In the communications equipment room, install a 30-foot long service loop on each end of fiber optic cable.  Copper cables shall take the longest path around the room prior to landing on racks.

          - Pulling Cable:  Comply with BICSI ITSIM, Ch. 4, "Pulling Cable."  Monitor cable pull tensions.

        - UTP Cable Installation:

          - Comply with ANSI/TIA-568-C.2.

          - Do not untwist UTP cables more than 1/2 inch from the point of termination to maintain cable geometry.

        - Optical Fiber Cable Installation:

          - Comply with ANSI/TIA-568-C.3.

          - Cable shall be terminated on connecting hardware that is rack mounted.

          - All optical fiber cable installed shall be provided with supplemental protection.  (1” minimum innerduct.)

        - Group connecting hardware for cables into separate logical fields.

See Editing Instruction No. 5 in the Evaluations for discussion about EMI.

        - Separation from EMI Sources:

          - Comply with BICSI TDMM and ANSI/TIA-598-C recommendations for separating unshielded copper voice and data communication cable from potential EMI sources, including electrical power lines and equipment.

          - Separation between open communications cables or cables in nonmetallic raceways and unshielded power conductors and electrical equipment shall be as follows:

            - Electrical Equipment Rating Less Than 2 kVA:  A minimum of 5 inches.

            - Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 12 inches.

            - Electrical Equipment Rating More Than 5 kVA:  A minimum of 24 inches.

          - Separation between communications cables in grounded metallic raceways and unshielded power lines or electrical equipment shall be as follows:

            - Electrical Equipment Rating Less Than 2 kVA:  A minimum of 2-1/2 inches.

            - Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 6 inches.

            - Electrical Equipment Rating More Than 5 kVA:  A minimum of 12 inches.

          - Separation between communications cables in grounded metallic raceways and power lines and electrical equipment located in grounded metallic conduits or enclosures shall be as follows:

            - Electrical Equipment Rating Less Than 2 kVA:  No requirement.

            - Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 3 inches.

            - Electrical Equipment Rating More Than 5 kVA:  A minimum of 6 inches.

          - Separation between Communications Cables and Electrical Motors and Transformers, HP and Larger:  A minimum of 48 inches.

          - Separation between Communications Cables and Fluorescent Fixtures:  A minimum of 12 inches.

        - A pull string shall be installed in all conduits, including those with cables installed.  String shall be securely tied off at both ends.

      - FIRESTOPPING

        - Comply with requirements in Division 07 Section "Penetration Firestopping."

        - Comply with ANSI/TIA-569-C, Annex A, "Firestopping."

        - Comply with BICSI TDMM, "Firestopping Systems" Article.

      - GROUNDING

        - Install grounding according to BICSI TDMM, "Grounding, Bonding, and Electrical Protection" Chapter.

        - Comply with ANSI-607-B.

        - Locate grounding bus bar to minimize the length of bonding conductors.  Fasten to wall allowing at least 2-inch clearance behind the grounding bus bar.  Connect grounding bus bar with a minimum No. 4 AWG grounding electrode conductor from grounding bus bar to suitable electrical building ground.

        - Bond metallic equipment to the grounding bus bar, using not smaller than No. 6 AWG equipment grounding conductor.

Retain subparagraph below if screened twisted-pair cables and coaxial cables are in communications equipment rooms.

          - Bond the shield of shielded cable to the grounding bus bar in communications rooms and spaces.

      - IDENTIFICATION

Retain one of first two paragraphs below.

        - Identify system components, wiring, and cabling complying with ANSI/TIA-606-B.   The identification scheme shall be coordinated with the owner prior to any labeling or testing.

See Evaluations for discussion about designating the class of cabling plant administration and color-coding of cross-connect fields.

        - Comply with requirements in Division 09 Section "Interior Painting" for painting backboards.  For fire-resistant plywood, do not paint over manufacturer's label.

See Evaluations for discussion about TIA/EIA standard as it applies to this Section.

        - Cable Schedule:  Post in prominent location in each equipment room and wiring closet.  List incoming and outgoing cables and their designations, origins, and destinations.  Protect with rigid frame and clear plastic cover.  Furnish an electronic copy of final comprehensive schedules for Project.

        - Cabling Administration Drawings:  Show building floor plans with cabling administration-point labeling.  Identify labeling convention and show labels for telecommunications closets, backbone pathways and cables, entrance pathways and cables, terminal hardware and positions, horizontal cables, work areas and workstation terminal positions, grounding buses and pathways, and equipment grounding conductors.  Follow convention of ANSI/TIA-606-B.  Furnish electronic record of all drawings, in software and format selected by Owner.

        - Cable and Wire Identification:

          - Label each cable within 4 inches of each termination and tap, where it is accessible in a cabinet or junction or outlet box, and elsewhere as indicated.

          - Label each terminal strip and screw terminal in each cabinet, rack, or panel.

            - Individually number wiring conductors connected to terminal strips, and identify each cable or wiring group being extended from a panel or cabinet to a building-mounted device shall be identified with name and number of particular device as shown.

            - Label each unit and field within distribution racks and frames.

          - Identification within Connector Fields in Equipment Rooms and Wiring Closets:  Label each connector and each discrete unit of cable-terminating and connecting hardware.  Where similar jacks and plugs are used for both voice and data communication cabling, use a different color for jacks and plugs of each service.

          - Both ends of all backbone cable shall be labeled.  Labels will be self laminating and machine generated.  The label shall contain the following information:

            - The Origination (TR it is feeding from).

            - The Destination (TR it is feeding).

            - Number of pairs or fibers

          - Both ends of all horizontal cables shall be labeled.  Labels shall be self-laminating and machine generated.  The cable, workstation faceplate, panel ports and block positions shall be labeled with the room number, location in room, outlet type & # (data D1, D2, etc).   In rooms with multiple outlets, label clockwise as you enter the room: 1, 2, 3 e.g. a data port at the first drop location to the left of Room 216 door would be (216-1 D1).  When terminating workstation cables in the TR, organize and label the cables in numeric room number order at the patch panel.

          - CNS will approve all labeling schematics prior to installation. "As-Built" drawing with all outlets identified shall be provided.

        - Labels shall be self-laminating or computer-printed type with printing area and font color that contrasts with cable jacket color.  Handwritten labels will not be acceptable.

          - Cables use flexible vinyl or polyester that flex as cables are bent.

      - FIELD QUALITY CONTROL

Retain one of first two paragraphs below to identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second paragraph, retain "Field quality-control reports" Paragraph in "Submittals" Article.

Retain first paragraph below to require Contractor to perform tests and inspections.

        - Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.

        - Tests and Inspections:

          - Visually inspect UTP and optical fiber cable jacket materials for NRTL certification markings.  Inspect cabling terminations in communications equipment rooms for compliance with color-coding for pin assignments, and inspect cabling connections for compliance with ANSI/TIA-568-C.1.

          - Visually confirm Category  marking of outlets, cover plates, outlet/connectors, and patch panels.

          - Visually inspect cable placement, cable termination, grounding and bonding, equipment and patch cords, and labeling of all components.

          - Test UTP backbone copper cabling for DC loop resistance, shorts, opens, intermittent faults, and polarity between conductors.  Test operation of shorting bars in connection blocks.  Test cables after termination but not cross-connection.

            - Test instruments shall meet or exceed applicable requirements in ANSI/TIA-568-C.2.  Perform tests with a tester that complies with performance requirements in "Test Instruments (Normative)" Annex, complying with measurement accuracy specified in "Measurement Accuracy (Informative)" Annex.  Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

          - Optical Fiber Cable Tests:

            - Test instruments shall meet or exceed applicable requirements in ANSI/TIA-568-C.1.  Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

            - Link End-to-End Attenuation Tests:

              - All multimode fiber cables shall be tested at both 850 nm and 1300 nm after installation. Printed test results for each fiber strand are required. All tests are to be performed in accordance with ANSI/TIA/EIA-526-7, Method A.1, One Reference Jumper. Fibers will be considered acceptable if the OTDR trace for that fiber shows an end to end loss of less than xxdB + yy(0.2)dB + zz(0.5)dB (where yy is the number of splices, zz is the number of connector pairs and xx is calculated using the following formula: xx = distance X fiber attenuation/unit distance @ lambda). In addition, no splice may show a loss of greater than 0.2 dB and no connector pairs may show a loss of greater than 0.5 dB. Any additional tests required by the ANSI/TIA/EIA standard shall also be performed and also included in the written test report.

              - The vendor shall perform tier 2 testing on each fiber strand utilizing a OTDR bi-directional tester at the wavelengths specified above. Overall, the OTDR test results shall be made up of the wavelength of the conducted test, the link length, attenuation, cable identification, the locations of the near end, the far end and each splice point or points of discontinuity. Hard-copy and electronic copy results for each fiber strand shall be submitted as part of "As- Built" documentation.

          - UTP Performance Tests:

            - Test for each outlet.  Perform the following tests according to ANSI/TIA-568-C.1 and ANSI/TIA-568-C.2:

              - Wire map.

              - Length (physical vs. electrical, and length requirements).

              - Insertion loss.

              - Near-end crosstalk (NEXT) loss.

              - Power sum near-end crosstalk (PSNEXT) loss.

              - Equal-level far-end crosstalk (ELFEXT).

              - Power sum equal-level far-end crosstalk (PSELFEXT).

              - Return loss.

              - Propagation delay.

              - Delay skew.

Retain first subparagraph below when cable is used for broadband closed-circuit television applications.  Revise to suit tests to verify cable performance for other systems using coaxial cable.

          - Final Verification Tests:  Perform verification tests for UTP, and optical fiber systems after the complete communications cabling and workstation outlet/connectors are installed.

            - Data Tests:  These tests assume the Information Technology Staff has a network installed and is available to assist with testing.  Connect to the network interface device at the demarcation point.  Log onto the network to ensure proper connection to the network.

        - Document data for each measurement.  Data for submittals shall be printed in a summary report that is formatted similar to Table 10.1 in BICSI TDMM, or transferred from the instrument to the computer, saved as text files, and printed and submitted.

        - If the cable or termination fails to meet the above requirements, it shall be replaced by the contractor at the contractor’s expense.

See Division 01 Section "Quality Requirements" for retesting and reinspecting requirements and Division 01 Section "Execution" for requirements for correcting the Work.

        - Prepare test and inspection reports documenting compliance with all requirements of these specifications.  Provide three (3) printed copies and two (2) compact disks of all data.

      - The Contractor shall provide a system warranty covering the installed cabling system against defects in workmanship, components, and performance, and covering follow-on support after project completion.

      - WARRANTIES

        - INSTALLATION WARRANTY.  The Contractor shall warrant the cabling system against defects in workmanship for a period of one year from the date of system acceptance.  The warranty shall cover all labor and materials necessary to correct a failed portion of the system and to demonstrate performance within the original installation specifications after repairs are accomplished.  This warranty shall be provided at no additional cost to the Owner.

        - Copper drops shall be warranted to results defined in the channel specifications of ANSI/TIA-568-C.2 Category 6 up to 250MHz.

        - Fiber optic links shall be warranted to the link and segment performance minimum expected results defined in ANSI/TIA-568-C.1.

END OF VOICE/DATA SYSTEM