SECTION 270640 – CATV DISTRIBUTION SYSTEM

- SCOPE OF WORK

  - Furnishing of all labor, project management, materials, tools, equipment necessary for the complete installation of a CATV Distribution System as shown on the plans and as herein specified.

  - The Electrical Contractor shall provide conduit systems from box to cable tray and mount all boxes for the Systems wiring. The Systems supplier shall provide special boxes for installation by the Electrical Contractor.

  - It is the intent of these specifications and the accompanying plans that the Contractor furnishes and installs a system complete in every respect and ready to operate.  All miscellaneous items and accessories required for such installation, whether or not each such item or accessory as shown on the plans or mentioned in these specifications, shall be furnished and installed.

  - It shall be the responsibility of each bidder to examine the site, plans and specifications carefully before submitting his bid, with particular attention to errors, omissions and conflicts between city ordinances, plans and specifications.  Any such discrepancy discovered shall be brought to the attention of the Engineer and will be included in the Base Bid.

  - SUBMITTALS

    - Provide complete brochure information on all components and accessory equipment with the bid documents. All information shall be clearly marked to indicate items provided.

    - Contractors wishing to propose systems which differ in any features, functions or operating characteristics other than those outlined in these specifications must do so in writing to the specifying authority at least ten (10) days prior to bid opening.  Proposals must include detailed information showing all deviations from the system as specified.  Final approval of the alternate system shall be based on the decision of the Owner.

  - REGULATORY LISTING

    - UL LISTING

All Material and equipment shall be listed, labeled, or certified by Underwriters Laboratories, Inc.  All power supplied and computers shall be UL listed.  Provide UL listing cards for all components specified herein.

- PRODUCTS, PERFORMANCE CRITERIA

  - The system shall comply with the radiation limitations as set forth under Part 15 as amended of the FCC Rules.

  - All equipment shall be designed and rated for 110 volt, 60 cp's AC operation and shall be UL rated for 24-hour day continuous operation.

  - The system shall have a signal to noise ratio of 43 dB or greater.

  - The overall system frequency response shall be flat to +/- 1 1/2 dB across the 6-megacycle bandwidth of any television channel.

  - The overall system shall have a voltage standing wave ratio of 1.2 to 1 or less.

  - The design and installation of the system shall be such that extensions, additions, or modifications will be possible without altering the system requirement of a voltage standing wave ratio of 1.2 or less.

  - The signal at any output shall not be less than 1000 microvolts or more than 10,000 microvolts into 75 ohms, except that in areas where direct pickup is possible, the signal shall not be less than 3000 microvolts. The signal at each outlet shall equal or exceed in quality the signal available from the Cable TV Company and shall be within 15 dB of same signal at any other outlet of the system.

  - Extraneous signal pickup shall be at least 50 dB down from desired normal minimum signal level.

  - Isolation between outputs and outlets shall not be less than 24 dB.

  - Upon completion of the system installation it shall be the responsibility of the Contractor to perform the necessary adjustments and balancing of all signals and amplifier level controls to insure proper system operation.

  - Each cable feeder line shall be inspected for proper termination.

  - Signal-to-noise test shall employ a Jerrold Model 727 field strength or equivalent. Measurements shall be made at the output of the last amplifier in the system. With the normal levels in the system the field strength meter shall be tuned to the picture carrier of each channel in turn and the reading obtained on the meter noted. The signal shall then be removed and the input of the head end amplifier shall be terminated in 75 ohms. With the field strength meter read the level of remaining noise in the absence of the signal and add a meter correction factor of 4 dB to the reading. The difference between the two readings will give the system's signal-to-noise ratio, and shall not be less than 43 dB.

  - No visible components of cross channel intermodulation ghosting or beat interference shall appear on the screen of a receiver turned to any normal signal.

  - Should such a demonstration of performance show that the Contractor has not properly balanced the system and that picture degradation is present or that output gain is not as specified, the Contractor shall make all necessary changes or adjustments and a second performance demonstration will be arranged at no cost to the Owner.

- EQUIPMENT

  - DISTRIBUTION AMPLIFIERS

    - The distribution amplifiers shall be a 19" rack mount, completely solid-state unit for the amplification of TV channels 2-61. Output level for each channel shall be +46dbmV minimum with no visible distortion.

    - Amplifier gain controls shall be provided with minimum of 15db control range. Typical amplifier gain shall be 51db.

    - The distribution system shall contain built-in regulated power supply to prevent change in output capability, and output level with changes in A-C line voltage of 117 VAC. Systems without regulated power supplies shall not be accepted.

    - Amplifier shall be a Blonder-Tongue, RMDA 450-50 or equal.

  - SPLITTERS

    - "2" way line splitters shall have a flat frequency response over the entire operating band from 500 to 600 MHz. The unit shall be of the hybrid design with a 75-ohm match of 17.0 dB RL minimum on all inputs and outputs. Output isolation shall be not less than 27.0 dB.

    - "4" way line splitters shall have a flat frequency response over the entire operating band from 500-600 MHz minimum on all input and outputs. Output isolation shall be not less than 27.0 dB.

    - Splitters shall be Blonder-Tongue Model CRS-2 and CRS-4 or equal.

  - CABLES

    - Each reel of coaxial cable used in the system shall be sweep tested for transmission and structural return loss and be so certified in writing by the cable manufacturer. Transmission sweep tests shall establish conformance to guaranteed loss value from 20-108 MHz 174-216 MHz and 470-890 MHz. Structural return loss tests by sweep method shall show a minimum return loss of 26 dB RL VHF, 16 dB RL UHF, as compared to a fixed 75-ohm reference from 20-108 MHz 174-216 MHz and from 470-890 MHz.

    - Coaxial cables shall be run in continuous lengths except for terminations and no splices shall be permitted in any conduit run. Cables shall be installed to avoid sharp bends or physical distortion.

    - All cables terminating at amplifiers or splitters shall be tagged as to function and destination.

    - The coax cable to rooms shall be plenum ratedRG-6/U coaxial cable with the following properties:

      - Nominal impedance: 75 ohms

      - Minimum center conductor size: 22 AWG solid

      - DC resistance maximum: 50 ohms/M

      - Nominal capacitance: 19 pF/ft + or 1 15%

      - Shield coverage minimum: 95%

      - Minimum number of shields: 2

      - Dielectric jacket type: plenum rated

      - Nominal velocity of propagation: greater than 70%

      - 100% sweep tested 5 - 500 MHz

    - All trunk cable shall be plenum rated RG-11U type.

  - DIRECTION TAPOFFS

    - All 1,2, or 4 tapoffs shall have a frequency range of 5 to 600 MHz.

    - All tapoffs must meet all CATV and SMATV requirements for RF shielding.

    - A variety of isolation valves shall be available to balance all signal levels.

    - Tapoffs shall be equal to Blonder Tongue CRT series or equal.

  - TV WALL PLATES

Provide a feed through F connector wall plate.

  - AGILE CHANNEL PROCESSORS

The processor shall be a Digital agile, solid state heterodyne processor equipped with Emergency Alert System alternate IF input.  The processor shall also have an externally accessible IF loop. The processor shall have a field selectable block upconverter to be able to accept sub-band input channels.  The processor shall have dual SAW filters to assure proper adjacent channel rejection and delayed AGC circuitry to automatically compensate for input variations.  The processor shall be capable of moving any input channel, to any output channel, as defined in the specifications below. The processor shall be equal to Blonder Tongue Model No. AQD-ATSC/QAM.  Provide chassis and power supplies as required.

  - CHANNEL MODULATORS

The channel modulators shall be part of modular headend system.  The rack chassis shall have positions for up to 12 modulator or demodulator modules.  The chassis shall be equal to Blonder Tongue MIRC-12 chassis with MIPS-12 power supply.  The channelized, heterodyne audio/video modulator shall be able to provide an audio and video modulated RF carrier output on any single VHF channel in the 54 to 400 MHz range.  The output level shall be +38 dBmV.  Channel selection shall be as directed by the Owner.  The unit shall be equal to Blonder Tongue model MICM.  Provide 18 modules for this project.  Channel Modulators shall be digital.  Signal is provided from Dish Network receivers (by owner), output to system shall be analog.

  - PASSIVE COMBINERS

Provide passive combiners to combine the outputs of multiple modulators and Processors.  These units shall feature high isolation between ports and a low net combining loss from each of the broadband inputs. Provide units as required to accommodate the total number of channels for this project.

  - EQUIPMENT HOUSING

Provide all cable TV headend equipment in paging/intercom rack.  Provide two 120VAC, 20 Amp power circuits in equipment housing for headend equipment.

- EXECUTION

  - INSTALLATION

    - Install cable in conduit or cable tray, which is provided by Division 26.

    - All penetrations in smoke or firewalls shall be sealed with fire stop rated for this purpose.

    - Provide for adequate ventilation in all equipment racks and take precautions to prevent electromagnetic or electrostatic hum.  The installation of all work shall be neat and of professional quality.  Cooperate with other trades in order to achieve well-coordinated progress and satisfactory final results.  Execute without claim for extra payment minor moves or changes in equipment locations to accommodate equipment of other trades or the architectural symmetry of the facility.

  - WIRING

It shall be the responsibility of the Contractor to furnish and install all plenum rated cable as required to provide a complete and operable system. Cable shall be properly supported above ceilings.

  - TESTING

    - Upon completion of the installation, the system must be tested by the manufacturer's representative and all necessary modifications and/or adjustments must be made to assure compliance with this specification.

    - All final signal dB levels of TV outlets and amplifier inputs and outputs shall be shown on as built drawings.

  - CERTIFICATION

Upon completion of the testing, the manufacturer or representative shall issue to the Owner a letter of certification attesting to the fact that he has tested and adjusted the system, that all components are properly installed and free of defects, and that the system is in compliance with this specification.

  - INSTRUCTION

The work shall include supplying the services of a field service representative who shall be a full-time employee.  The field service representative shall have specialized experience in the operation and maintenance of the system and shall instruct the Owner's personnel in the techniques involved in the operation of the systems.  A formal on-site training shall be provided by the Contractor to the owner's representative/maintenance personnel and shall include instructions in the location, inspection, maintenance, testing and operation of all components.  Provide a signed copy of the name of the personnel giving the instructions and the personnel of the Owner.

  - DIAGRAMS, DRAWINGS AND INSTRUCTION MANUALS

Furnish bound instruction manuals for the complete system for the Owner's use.  Manuals shall include instructions, block and schematic diagrams, wiring diagrams, specification and technical data of the components and "as-built" drawings of the completed system.

  - WARRANTY, SERVICE AND MAINTENANCE

Provide a one-year warranty of the installed system, against defects in material and workmanship.  If any defects are found within the warranty period, the defective equipment shall be replaced at no extra charge to Owner for parts or labor.

END OF CATV DISTRIBUTION SYSTEM