SECTION 262726 - WIRING DEVICES AND PLATES

- GENERAL

  - This section of the specifications includes wiring devices, cover plates, weatherproof and dust-tight closures, communications devices and floor outlets.

  - Wiring devices are listed by manufacturer and catalog numbers to establish the quality and type required.  Equivalent devices of other manufacturers will be acceptable with prior approval of the Engineer.  Submit cutsheets and/or samples of each type ten days prior to bid date for review and written approval to bid.  Insofar as possible, standard application or special application devices shall be by one manufacturer.

- MATERIALS

| TYPE | RATING | CONFIGURATION | COLOR | VENDOR - CAT. # |
| --- | --- | --- | --- | --- |
| RECEPTACLE - DUPLEX COMMERCIAL GRADE | 125V, 20A | NEMA 5-20R |  | HUBBELL CR5362 GE 5362 LEVITON 5362 |
| RECEPTACLE - DUPLEX G.F.I. (SHALL MEET U.L. 943 STANDARD) | 125V, 20A | NEMA 5-20R |  | HUBBELL GFR5352A NO SUBSTITUTIONS |
| RECEPTACLE - SIMPLEX | 125V, 20A | NEMA 5-20R |  | HUBBELL 5361 |
| RECEPTACLE - DUPLEX, SAFETY TYPE (WITH TAMPER-RESISTANT SCREWS) | 125V, 20A | NEMA 5-20R |  | HUBBELL HBL-8300-SG |
| RECEPTACLE - DUPLEX, SAFETY TYPE (WITH TAMPER-RESISTANT SCREWS) | 125V, 15A | NEMA 5-15R |  | HUBBELL HBL-8200-SG |
| RECEPTACLE, DUPLEX NEON PILOT FACE-RED | 125V, 15A | NEMA 5-15R |  | HUBBELL 5262-LHR GE 5362-LHR LEVITON 5362-LHR |
| RECEPTACLE, SIMPLEX WITH CLOCK HANGER TAB, STAINLESS STEEL PLATE | 125V, 15A | NEMA 5-15R | METAL | HUBBELL 5235 LEVITON 658-BR ARROW-HART 5760 |
| RECEPTACLE, DUPLEX ISOLATED GROUND (WITH ORANGE LEGEND PLATE) | 125V, 20A | NEMA 5-20R | ORANGE | HUBBELL IG-5362 GE 5362-IG LEVITON 5362-IG |
| RECEPTACLE, DUPLEX HOSPITAL GRADE (TO BE USED IN ALL PATIENT CARE AREAS, PER N.E.C., ART. 517) | 125V, 20A | NEMA 5-15R NEMA 5-20R |  | HUBBELL 8200H GE 8200 LEVITON 8200 HUBBELL 8200H GE 8300 LEVITON 8300 |
| RECEPTACLE, DUPLEX RED COLOR NYLON FACE (FOR EMERGENCY POWER OUTLETS) | 125V, 20A | NEMA 5-20R | RED | HUBBELL 5352-RDB GE 5362-RDB LEVITON 5362-RDB |
| RECEPTACLE, DUPLEX ISOLATED GROUND WITH SURGE SUPPRESSION, INCLUDING INDICATOR LIGHT | 125V, 15A | NEMA 5-15R | BLUE DEVICE | HUBBELL 5250S LEVITON 5380 ARROW-HART 5362 |
| RECEPTACLE, SINGLE | 250V, 20A | NEMA 10-20R | BLACK | HUBBELL 6810 GE 4124 LEVITON 5032 |
| RECEPTACLE, SINGLE | 250V, 30A | NEMA 6-30R | BLACK | HUBBELL 9330 GE 4139 LEVITON 5372 |
| RECEPTACLE, SINGLE | 250V, 50A | NEMA 6-50R | BLACK | HUBBELL 9367 GE 4141 LEVITON 5374 |
| SWITCH, SINGLE POLE | 120/277V, 20A | SPST |  | HUBBELL HBL-1221 GE 5951 LEVITON 1221 |
| SWITCH, SINGLE POLE - RED TOGGLE (WITH RED COVER PLATE, FOR EMERGENCY LIGHTING CONTROL) | 120/277V, 20A | SPST | RED | HUBBELL HBL-1221-RDB GE 5951-RDB LEVITON 1221-RDB |
| SWITCH, THREE-WAY | 120/277V, 20A | 3-WAY |  | HUBBELL HBL-1223 GE 5953 LEVITON 5953 |
| SWITCH, FOUR-WAY | 120/277V, 20A | 4-WAY |  | HUBBELL HBL-1224 GE 5954 LEVITON 5954 |
| SWITCH, KEYED | 120/277V, 20A | SPST | N/A | HUBBELL HBL-1221-L GE 5951-L LEVITON 1221-L |
| SWITCH, KEYED | 120/277V, 20A | 3-WAY | N/A | HUBBELL HBL-1223-L GE 5953-L LEVITON 1223-L |
| SWITCH, KEYED | 120/277V, 20A | 4-WAY | N/A | HUBBELL HBL-1224-L GE 5954-L LEVITON 1224-L |
| NOTE: SWITCH, KEYED TO EACH BE FURNISHED WITH ONE HUBBELL #1209 KEY. TURN OVER TO OWNER AT CLOSE OF PROJECT AND OBTAIN RECEIPT FOR VERIFICATION THAT KEYS HAVE BEEN DELIVERED. |  |  |  |  |
| SWITCH, MOMENTARY, 3-POSITION, CENTER OFF SWITCH, PILOT (TOGGLE LIT IN OFF POSITION) | 120/277V, 20A (VERIFY VOLTAGE USED) | SPDT |  | HUBBELL HBL SERIES GE EQUIVALENT LEVITON EQUIVALENT |
| SWITCH, PILOT (TOGGLE LIT IN OFF POSITION) | 120/277V, 20A (VERIFY VOLTAGE USED) | SPDT OR AS NOTED | CLEAR "LEXAN" | HUBBELL HBL SERIES GE EQUIVALENT LEVITON EQUIVALENT |
| SWITCH, PILOT (TOGGLE LIT IN ON POSITION) | 120/277V, 20A (VERIFY VOLTAGE USED) | SPST OR AS NOTED | CLEAR "LEXAN" | HUBBELL HBL-PL7 SERIES GE EQUIVALENT LEVITON EQUIVALENT |
| TIMER SWITCH | 120V | SPST, 15 MINUTE |  | NUTONE VS63 GE EQUIVALENT LEVITON EQUIVALENT |
| NOTES: 1. PROVIDE MATCHING CAP (PLUG) FOR ALL RECEPTACLES 30 AMP RATED AND ABOVE AS REQUIRED FOR EQUIPMENT. 2. ALL RECEPTACLES SHALL BE BACK OR SIDE-WIRED, CLAMPING TYPE - FOR DRYERS AND RANGES, PROVIDE 3-POLE GROUNDING TYPE AS REQUIRED BY DEVICE. LOCATE DEVICE SO THAT DRYER OR RANGE CAN BE PUSHED TIGHTLY AGAINST WALL. - RECEPTACLES SHALL BE TAMPER RESISTANT AND WEATHER RESISTANT AND MARKED ACCORDINGLY AS REQUIRED BY N.E.C. - ALL RECEPTACLES INSTALLED IN DAMP OR WET LOCATIONS SHALL BE UL LISTED WEATHER RESISTANT TYPE.  SEE ARTICLE 3, COLOR. |  |  |  |  |

  - Small Motor Control Switches:

    - For small line-to-neutral motor loads of 3/4 HP or less, single phase, rated at 120 or 277 volts, provide snap-type, H.P. rated motor starter switch with thermal overloads.  Overload heaters sized to match the motor nameplate amperes and the ambient temperature shall be provided.  Provide with NEMA 1, NEMA 3R or other enclosure suitable for the location and atmosphere.  All manual starters in finished areas shall be in flush-mounted enclosures.

- COLOR

  - Color of devices shall be as selected by the architect.  Samples (devices, plates or both) may be required to be submitted with other architectural color items by the Contractor.  The Contractor shall coordinate any such submission required with other trades, the Prime Contractor or as needed.

  - Where devices are controlling or supplying emergency power from a standby source, the device color shall be red, as with switch toggles or receptacle fronts.  Plate color shall match others on normal power in the building unless otherwise noted.

  - Where surface finishes next to the devices vary in color or shade throughout the project, the Contractor may be required to provide lighter or darker plates and devices to more closely match wall finishes.  These variations are considered to be included in the original contract for construction.

- MANUAL DIMMERS

  - Manual dimmers shall be provided with all solid state components, complete with choke coil and/or other R.F.I. suppression devices.

  - Manual dimmers shall be suitable for mounting in single gang outlet box, ganging together in multi-section boxes where indicated, without derating being necessary.

  - Manual dimmers for fluorescent lighting or low voltage transformer-fed incandescent fixtures shall be matched to suit the characteristics of the particular manufacturer's electronic ballast or transformer used in the dimming - type fixture.  Submit shop drawings of dimmer in the same submittal as the lighting fixtures.

- PLATES AND COVERS

  - Unless otherwise specified or noted, all wiring device plates and covers shall be smooth thermoplastic, Hubbell "P" Series or equivalent G.E. or Leviton.  Color shall match device unless otherwise indicated.

  - Cover plates shall be of one manufacturer insofar as possible.

  - Weatherproof plates for G.F.C.I. receptacles shall be cast aluminum, self-closing, gasketed, suitable for standard box mounting, U.L. listed for wet location use, cover closed.  Vertical mounting - Hubbell WP26M, horizontal mounting - Hubbell WP26MH (die-cast zinc) or equivalent Leviton or G.E.

  - Weatherproof switch plates for toggle-handle switches shall be clear silicone rubber, for standard outlet boxes.   Hubbell 1795 or equivalent G.E. or Leviton.

  - Cover plates for computer, telephone or other system outlets shall be as required to meet supplier or the owner's requirements, as applicable.  Color to match other plates on project.  Furnish telephone plates with wall-mounting studs if mounted at 48" or higher.  See devices schedule below.

- STANDARD SINGLE-SERVICE FLOOR BOXES

  - In general, floor boxes to be used flush in concrete floors shall be of single-gang stamped steel construction, round, deep style, fully adjustable Hubbell B-2537 Series, Type 1 or equivalent.

  - Where multiple gangs are indicated on the plans (or elsewhere), multi-gang (up to 3 yokes maximum) stamped steel, rectangular, deep style units shall be used.  They shall be fully adjustable, Hubbell B-2432 Series, Type 1, or equivalent.  Multiple-gang boxes shall be provided with removable partitions between each section in accord with N.E.C., where power and non-power circuits enter the same box.

  - In general, all cover plates for floor boxes shall be flush, solid brass. Provide typical plates as listed:

Duplex Outlet		- Round, Duplex Flap - Hubbell S-3925

- Rectangular, Duplex Flap - Hubbell S-3825

Telephone or Data	- Round, Combination 1" or 2 1/8" - Hubbell S-2725

- Rectangular, Combination 1" or 2 1/8" - Hubbell S-2625

  - Furnish floor boxes with threaded hubs as required to suit conduit routings, 3/4" minimum.

  - Furnish carpet flanges for all boxes installed in carpeted areas.  Flanges to be clear polycarbonate plastic, round - Hubbell S-3079 or rectangular, for gangs indicated - Hubbell S-308 Series or equivalent.

  - Floor outlet boxes shall be installed dead level flush with wood, VCT, concrete or other hard surface type floor.  Furnish special stop trims for terrazzo where required.

  - Outlets within floor boxes shall be as specified elsewhere in these specifications.

- SPECIAL MULTI-SERVICE FLOOR BOXES

  - In general, floor boxes that are to contain multiple services such as power, data, voice, video, etc., shall be constructed of stamped steel and heavy thermoplastic with barriers or compartments to separate power from signal services per National Electrical Code.

  - Provide multi-service floor boxes with proper trim for carpet, wood, terrazo, tile or concrete floors, wiring slots, dust covers and proper device plates to hold outlets, jacks, etc.  They shall be fully adjustable.  Conduit rough-in shall be as required.  All tops shall be capable of receiving an insert of the surrounding floor material.

  - Outlets for multi-service floor boxes shall be as specified elsewhere in these specifications.

  - Set boxes dead level with flooring and provide proper support by thickening concrete slab, welding angle iron across joists below or other approved means.

  - Multi-service floor boxes shall be capable of containing a minimum of two duplex receptacles and two 4-position single gang modular plates for voice, video or data jacks and shall be as manufactured by Hubbell #HBLCFB401 base with #HBLTCGNT cover, with all required accessories or equivalent Walker “RFS” Series or Lew.  If not installed on carpeted floors, provide flush brass trim.

- INSTALLATION

  - All wiring devices in dusty areas, exposed to weather and moisture shall be installed in Type "FS" or similar conduit fittings having mounting hubs, with appropriate cover plates.

  - Devices that have been installed before painting shall be masked.  No plates or covers shall be installed until all finishing and cleaning has been completed.

  - Provide G.F.C.I. duplex feed-thru style receptacles in accordance with new U.L. Standard 943 where indicated or required by the National Electrical Code, whether specifically called out or not.  When a G.F.C.I. receptacle is on a circuit with other non-G.F.C.I. receptacles, it shall always be placed at the homerun point of the circuit and shall be wired to ground-fault interrupt protect the downstream outlets on that circuit unless specifically indicated to the contrary.  Provide a "G.F.C.I. protected" label on each downstream outlet.

  - GFCI devices shall be installed in a “readily accessible” location per NEC requirements.  GFCI protected outlets required by plans or code shall be fed by a GFCI breaker or upstream GFCI device if they are not readily accessible.

  - Where surge suppression outlets are provided, they shall be ANSI Category "A" style.  They shall be installed as dedicated-circuit outlets or where indicated with multiple outlets on a circuit, they shall be placed at the homerun point of that circuit and feed-thru wired to protect the downstream outlets on that circuit.

  - All receptacles shall be installed with ground prong at top position.

  - All outlets not provided with wiring devices shall be closed with a blank plate matching other plates in the area.

END OF WIRING DEVICES