SECTION 260506 - LIGHTNING PROTECTION SYSTEM

- GENERAL

  - Each Electrical Contractor's attention is directed to Section 26000, General Provisions-Electrical and all other contract documents as they may apply to his work.

- SCOPE OF THE WORK

  - The Electrical Contractor shall provide the necessary labor, materials, and services necessary to modify the lightning protection system as specified herein.  Contractor shall protect, repair, and modify the existing lightning protection system as necessary to comply with NFPA 780, current addition.

- QUALITY ASSURANCE

  - Manufacturers:  First regularly engaged in manufacturer of lightning protection equipment, of types, sizes and ratings required, whose products have been satisfactorily used in similar service for not less than 5 years.  The firm shall be a member of and certified by the Lighting Protection Institute of America.

  - Installer:  A firm with at least 3 years of success installation experience on projects with lightning protection work similar to that required for project.

  - ANSI/NFPA Compliance:  Comply with NEC and NFPA No. 780, "Standard for the Installation of Lightning Protection Systems", as applicable to materials and installation of lightning protection components and wiring.

  - ANSI Compliance:  Comply with applicable portions of ANSI C2 and C62.2 pertaining to lightning (surge) arrestors.

  - UL Compliance:  Comply with UL 96, "The Standard for Lightning Protection Components" and UL96A, “Installation Requirements for Lightning Protection Systems” pertaining to design, materials and sizing of lightning protection components.  Provide components which are UL listed and labeled.

- SUBMITTALS

  - Product Data:  Submit manufacturer's data on lightning protection systems and components.

  - Shop Drawings:  Submit dimensioned layout drawings of lightning protection system equipment and components including conductor routing and connections.

  - Maintenance Data:  Submit maintenance instructions for lightning protection system.  Include this data in maintenance manuals.

- MATERIALS

  - Acceptable Manufacturers

Available Manufacturers:  Subject to compliance with requirements, manufacturers offering lightning protection components which may be incorporated in the work include, but are not limited to, the following:

Conductors and Air Terminals:

Independent Protection Co., Inc.

Thompson Lightning Protection, Inc.

A/C Lightning Protection Co., Inc.

Protective Devices (Surge Arrestors):

General Electric Co.

TII Industries, Inc.

Atlantic Scientific Corp.

- LIGHTNING PROTECTION SYSTEM COMPONENTS:

  - General

    - Provide lightning protection system components of types, sizes, ratings for class of service indicated, which comply with manufacturer's standard materials, design and construction in accordance with published product information and as required for a complete installation.  Where more than one type of component meets requirements, selection is Installer's option.  Where type or material is not otherwise indicated comply with NFPA 780 and UL 96 standards.

  - Conductors

Class 1 Installations:

    - Main Conductors:  Aluminum cable; strand dia. 0.064"; 0.095#/ft.; 98,600 circular mils.

    - Secondary Conductors:  Aluminum cable; strand dia. 0.064"; 10 strands.

    - Air Terminals:  Aluminum for concealed installation; 10" point, 1/2" x 12" long solid aluminum stem, lead washer, support bracket and adjustable clamp type cable connector.

    - Connector:  Aluminum right-angle thru-roof cable connector; bronze and lead seal flashing washer, 1/2" x 8" threaded stem, to fit 6" roof thickness.

    - Connector:  4" aluminum parallel bonding clamp for connecting 1/0 or 2/0 cables.

    - Splicer:  Aluminum straight cable splicer for splicing No. 4 and No. 6 cables.

    - Splicer:  Aluminum pressure type "T" cable splicer for clamping standard cables through 2/0 with hex bolts and washers.

    - Splicer:  Bimetal straight splicer of cast aluminum and bronze for 2/0 cable with moisture tight sealing capability.

    - Ground Rod:  Solid copper, 5/8" dia. x 10'.

    - Rod Clamp:  4" bronze ground rod clamp for connecting cable, up to and including 2/0 and 5/8" or 3/4" ground rod.

    - Ground Plate:  Sheet copper plate, 36" x 36" x 20-gauge, with 2 cable attachments.

    - Bonding Plate:  8 sq. in. steel plate with 1" dia. bolt-hole for bonding cable to structural steel, with vice-grip type cable connector with 2" of cable contact.

    - Surge Arrestor:  Electrical service arrestor, solid state, 277/480V/30/4W for exterior mounting.

- EXECUTION - Installation of Lightning Protection Systems

  - Install lightning protection systems as indicated in accordance with equipment manufacturer's written instructions, in compliance with applicable requirements of NFPA No. 70 and 780 and with UL's lightning protection standards to ensure that lightning protection systems comply with requirements.

  - Coordinate with other work, including electrical wiring and roofing work as necessary to interface installation of lightning protection system with other work.

  - Install conductors with direct paths from air terminals to ground connections avoiding sharp bends and narrow loops.

  - Install arrestors as close as practical to equipment they are protecting.  Install appropriate unit at main electrical service entrance equipment.

  - Visually inspect all existing conductors.  Confirm all existing bolted connections are torqued to manufacturer’s recommendations.  Repair conductors and connections found to be damaged or poorly connected.

- TESTING

  - Refer to Division 26 Section “Grounding” for grounding electrode system requirements.

END OF LIGHTING PROTECTION SYSTEM