SECTION 201320 - GEOTHERMAL (EARTH COUPLED) LOOP PIPING SYSTEM

- GENERAL

  - The Contractor's attention is directed to the General and Special Conditions, General Conditions-Mechanical and to all other Contract Documents as they apply to this branch of the work.  Attention is also directed to all other sections of the Contract Documents which affect the work of this section and which are hereby made a part of the work specified herein.

- INSTALLATION PERSONNEL AND TRAINING REQUIRED

  - The loop installer, must have a current International Ground Source Heat Pump Association (IGSHPA) certification, having completed an IGSHPA training course in the fundamentals of design, installation, and operation of ground source systems, and having passed the IGSHPA certification examination.

  - Ground heat exchanger fabricators must have completed a heat fusion school in which each participant has performed a heat fusion procedure under direct supervision of a IGSHPA Certified Heat Fusion Technician.  The Fusion Technician must be thoroughly familiar with heat fusion procedures, and have had formal training at a heat fusion school under direct supervision of an IGSHPA certified instructor.

  - Local and state laws, ordinances, and regulations as they pertain to buried pipe systems shall be strictly followed.

- GROUND HEAT EXCHANGER MATERIALS

  - Piping shall be virgin polyethylene with a PE 4710 piping formulation and cell classification of 445576C or E per ASTM D 3350.  Pressure ratings are at 73.4° F.

  - 2" and smaller shall be SDR 9.   Pressure rating of 255 PSI.

  - 3" and larger shall be SDR 15.5 or Schedule 40.  Pressure rating of 135 PSI.

  - Markings

    - Sufficient information shall be permanently marked on the length of the pipe as defined by the appropriate ASTM pipe standard.

    - Piping shall also have permanent factory length markings.

  - Certification

    - Manufacturer shall supply a notarized document confirming compliance with the above standards.

  - Manufacturers

    - Centennial Plastics, Charter Plastics, Flying W Plastics, Lamson Vylon Plastics, Chevron Phillips, or Polypipe

  - Warranty

    - Manufacturer shall supply a written warranty of 25 years or greater, specifying material replacement and labor allowance.  This applies to all pipe, fittings, transitions, valves, etc. All Warranty periods shall begin at Substantial Completion.

- PIPE JOINING METHODS

  - The only acceptable method for joining buried pipe systems is by a heat fusion process.

  - Polyethylene pipe shall be butt or socket fused in accordance with pipe manufacturer's procedures.

  - Factory installed "U" bends shall be used at the bottom well bend.

- CASING

  - Casing shall be steel.  PVC casing is not acceptable.

  - The Contractor shall include in the bid an allowance for 10 feet of permanent left-in-place steel casing per each new geothermal well indicated on the drawings (excluding the previously installed test wells).  The actual amount of casing used per hole shall be tracked with a casing log and wellfield schematic.  Schematic shall depict geothermal wells and provide labels for each.  Log shall state the bore hole number (as depicted on the schematic), date and time casing was installed, and linear feet of casing left in place for each bore hole.  For example:

Bore hole # 1		8/1/09		2 P.M.	  30 feet of casing installed

Bore hole # 2		8/2/09		9 A.M.	  10 feet of casing installed

This log shall be kept current at all times and be signed daily during drilling by the well field installer, mechanical contractor, General Contractor and Owner’s representative.

  - Contractor shall submit a unit price for steel casing left in place on the Bid Form.

  - The casing log and the submitted casing unit price will be used to reconcile the Contract Amount with the actual amount of casing installed.  The Contractor will only be paid the full unit price for casing left in place.  Push and pull casing (temporary casing) will be paid at half the rate for casing left in place.

- GEOTHERMAL VAULT

  - General

This specification designates the requirements for the geothermal vault including internal pipe, fittings, and valves.

  - External Shell

Shall be constructed of a high density polyethylene flat stock having a cell classification of 345444 with a UV stabilizer of C.  All materials used shall have a minimum thickness of 1”.  Internal and external seams are heat welded using high density polyethylene welding rods having a cell classification of 345444C.   Provide with a 30” manhole. The manhole lid is connected with 8-3/8” stainless steel counter sunk bolts.  Lid to have 5000 pound load bearing capacity.

  - Internal Bracing

Shall be spaced at a maximum of 30” and constructed of a minimum of 1” thick high density polyethylene flat stock heat welded to the external shell with high density polyethylene welding rods.

  - Internal Piping

Shall be constructed of Drisoplex 5300 Climate Guard High Density Polyethylene SDR 15.5 pipe having a cell classification of 345444 with a UV stabilizer of C.  This internal pipe is constructed in an offset, over and under, model for supply and return lines.  All joints to be heat fused.  The entire piping system to be tested using 150 psi nitrogen.  The main supply and return pipe to be shipped with cap butt welded to pipe.  All pipe penetrating the vault walls shall be SDR9 and heat welded to external shell.

  - Fittings

P/T Plugs:  Shall be constructed of solid brass and have a dual seal core of Nordel, good up to 350ºF for water.  Plugs shall be rated zero leakage from vacuum to 1000 psgi and are capable of receiving a pressure or temperature probe.  Each HPS & R pipe to the well field shall have a P & T port.

Butterfly Valve: Shall be constructed of a cast iron body, 416 stainless steel stem with a lever shut off system.

90º Elbows: Shall be molded out of high density polyethylene resins in accordance with the requirements of ASTM 3261.

Branch and Service Saddles: Shall be molded out of high density polyethylene resins in accordance with the requirements of ASTM 3261.

Valving: Each row of 10 wells shall have HPS & R shut off butterfly valve and each return line shall have a bell & gossett circuit setter for balancing.

Drain:  Provide a sump in the pit as well as a location for a pumped discharge.

  - Installation

The vault shall be lowered into a pit with a 6” bed of #57 gravel.  Once the vault is in its place, concrete is poured as recommended by the manufacturer in and around the vault to balance buoyancy pressure and allow for anchoring.  The manhole shall be flush with finished grade.

- FLUSHING, PURGING, PRESSURE AND FLOW TESTING

  - General

    - Coordinate this section with the cleaning and flushing listed in Section 230200 - HVAC Equipment.

    - All fusion joints and loop lengths shall be checked to verify that no leaks have occurred due to fusion joining or shipping damage.

  - Pressure Testing

    - Vertical loops shall be pressure tested before installation.  All horizontal components of the ground heat exchanger will be flushed, pressure and flow tested prior to backfilling. Pipes must contain fluid under pressure during backfilling.

    - Heat exchangers shall be tested hydrostatically at 150% of the pipe design rating or 300% of the system operating pressure if this value is the smaller of the two.  No leaks shall occur within a 48 hour period.  Engineer shall be notified when system is to be placed under pressure test.

  - Flushing and Purging

    - Notify the Engineer a minimum of 2 weeks in advance of system flushing.  The Engineer, Mechanical Contractor, Heat Pump Supplier, Test and Balance Contractor, and Well Field Installer shall all be present to observe system flushing and purging.  Schedule the system flushing to occur the same day as a regularly scheduled progress meeting. The Engineer MUST BE PRESENT.  Failure to notify the Engineer in advance will result in the Contractor having to flush the system a second time.

    - Flow rates shall be compared to calculated values to assure that there is no blockage or kinking of any pipe.  Submit this in writing to the Engineer.  Balance Contractor to verify.

    - A minimum velocity of 3 ft/sec in each piping section must be maintained until all air is removed.  Piping 8” and larger shall be purged at 4 ft/s minimum.  The system shall also be forward and reverse flushed to remove all debris. The building shall be flushed in sections as required to maintain high velocities.  Building mains shall be flushed separate from branches to maintain high velocity when flushing the mains.

    - Final purging of air from the entire building and loop field shall be performed by the Well Field Installer so that air in building piping will not be transferred to the well field.

    - The Balance Contractor must witness and confirm all pressure tests and flushing velocities along with confirm pressure drop for each geothermal well zone.

    - Contractor shall provide full size connection ports and valves as required to purge wellfield and building separately.

    - After the heat pump bypasses are flushed and the piping network is determined to be clean and free of air, the heat pumps themselves shall be flushed.

    - The system flushing device shall be equal to a Purge Pro Max distributed by Geothermal Supply Company.  The flushing pump shall provide performance equal to or exceeding the following values: 300 GPM at 125 PSI, dead head pressure of 128 PSI.  SUBMIT PUMP CURVE to Engineer for review and approval prior to system flush.  The flushing device shall provide means to release entrained air to the atmosphere and shall filter the water.  Filter shall be 50 micron.  Water shall be circulated and filters shall be changed until debris is no longer visible on filter.  Contractor shall provide filter media as required.

- HORIZONTAL PIPING SYSTEMS

  - Sharp bending of pipe around trench and bore hole corners must be prevented by using a shovel to round corners.  Manufacturer's procedures must be followed.

  - Backfilling procedure will include prevention of any sharp-edged rocks from coming into contact with the pipe by removal of the rocks before backfilling, backfilling through a coarse screen for a 6 inch cover, or use of a 6 inch cover of rock-free soil.  Clods resulting from use of a backhoe must be broken up so as not to form air pockets around the pipe which will reduce heat conduction between the earth and the pipe.  The flow of backfill soil must be controlled to prevent bridging and the formation of air pockets.  Several slow passes with an angled backfill blade are required.  Flooding is required to assure removal or air pockets.    Backfill load bearing capacity shall meet the Architect's specification where piping is located below asphalt.

  - Horizontal return bends must be backfilled by hand to properly support the pipes and prevent kinking.

  - All horizontal piping shall be a minimum of 42 inches below finished grade.

- BORE HOLE

  - The Contractor shall bore wells of a sufficient diameter to allow installation of the piping and U-bend, but shall be no less than 4-1/2".

  - The entire bore shall be grouted as recommended by IGSHPA with a thermally enhanced grout mixture with a thermal conductivity of 1.00 Btu/hr-ft-˚F.  Grout shall be GeoPro Thermal Grout Lite 100 bentonite mixture or approved equal.  Mixture shall be field mixed in strict accordance with manufacturer’s recommendations.  Grout mixture shall be mechanically pumped with a positive displacement pump into bore hole from bottom to top utilizing a tremie tube.  Through the course of the project, three sample grout specimens shall be taken of the mixed grouting material by this contractor.  An analysis shall be performed by the grout manufacturer to verify proper thermal performance and grout mixture.  This contractor shall submit these reports to the Owner, Architect and Engineer to verify compliance with the installation specifications.

  - If large water seams are encountered, bridging across water seams with #7 or #9 rock, or GeoPro Black Hills 3/8 inch Bentonite Plug, is acceptable.  The maximum height of the rock or bentonite bridge shall not exceed 8 feet.  The remainder of the vertical bore hole shall be grouted per the above specification.  Bore holes with water seams shall be monitored for settling of grout.  After a period of one week, all holes shall be topped off with grout as needed.  The Contractor shall continue to monitor holes that experience grout settling and continue to top off with grout throughout the warranty period.  Bore holes that are unable to hold grout shall be replaced with new bore holes at no cost.

  - The Contractor shall accept the site as-is and is responsible for any and all required casings.  If an area of voids is encountered, the Contractor shall either fill or re-drill wells in an approved area and extend piping to them.

  - No night drilling will be allowed.

  - Final Well-Field Survey: Engage a land surveyor to prepare a final geothermal well-field survey showing location of each geothermal well, underground valves, underground vaults, and routing of all underground piping for the Project.  Include on the survey a certification, signed by land surveyor, that principal metes, bounds, lines, and levels of Project are accurately positioned as shown on the survey.

Show relationship of well-field to existing property boundary lines, monuments, streets, site improvements and utilities, existing improvements and significant vegetation, adjoining properties, acreage, grade contours, and the distance and bearing from a site corner to a legal point.

A digital file for the existing property survey is available for use in locating the well-field and the property.

- DUST CONTROL

  - The Contractor is responsible for and shall provide dust control.  Dust shall not be allowed to leave the construction site boundaries, and furthermore, shall not be allowed to enter the building or accumulate on the building exterior.  When needed to meet these requirements, the Contractor shall provide and operate a mechanical dust collection system to control dust at the source.  Mechanical dust collection system shall consist of collection hood at the source ducted to a dust collector which separates dust from the airstream.  Dust shall be collected into sealed containers for disposal by the Contractor.

  - Water spraying may be used but shall not be considered a substitute for mechanical dust collection at the source when required.

- SURFACE WATER / MUD / SLURRY CONTROL

  - The Contractor is responsible for and shall provide control of all ground flowing fluids resulting from drilling operations.  The Contractor shall erect silt fences or other structures as required to contain drill cuttings, mud, slurry, etc. within the construction site boundaries.  In the event this requirement is not met, the Contractor shall provide all remediation measures as required by all authorities having jurisdiction over such events.

- WARRANTY

  - The entire ground loop system and backfill from a point 5 feet inside the building shall be warranted for five (5) years from date of substantial completion against any leakage or failure.  Warranty service for a pipe leak shall include recharging system with heat transfer fluid as originally specified, including glycol or ethyl alcohol if originally specified, as well as corrosion inhibitors.

- BALANCE

The Contractor shall assist the Balance Contractor in balancing the geothermal well zones to obtain the specified flows.

- SUBMITTALS

  - Submit manufacturer's specification sheets and installation instruction for each component of the system, showing manufacturer, pipe or tube weight, pressure rating, fitting type and joint type for each piping system.

  - Submit manufacturer's mechanical data for valves.

  - Submit a drawing indicating the system layout and pipe sizes.

  - Provide a copy of the technician's certification, and International Ground Source Heat Pump Association Certification.

- TEST BORES

  - Test bore information is included.  See next page.

  - The Contractor may visit the site prior to bid and perform their own test boring if additional information is required.  This shall be coordinated with the Owner.

END OF GEOTHERMAL