SECTION 201300 - PIPE, PIPE FITTINGS AND PIPE SUPPORT

- GENERAL

  - The Contractor's attention is directed to the General and Special Conditions, General Conditions-Mechanical and to all other Contract Documents as they apply to this branch of the work.  Attention is also directed to all other sections of the Contract Documents which affect the work of this section and which are hereby made a part of the work specified in this section.

  - When a pipe size is not indicated, the Contractor shall request the pipe size from the Engineers.  All piping shall be installed straight and true, parallel or perpendicular to the building construction.  Piping shall be installed so as to allow for expansion without damage to the building finishes, structure, pipe, equipment, etc., use offsets, U-bends or expansion joints as required. Where a section of piping is not indicated but is obviously required for completion of the system, the Contractor shall provide same at no additional cost to the project.  No mitered joints or field fabricated pipe bends shall be accepted.  Pipe shall clear all windows, doors, louvers and other building openings.

  - All pipe shall be supported in a neat and workmanlike manner and wherever possible, parallel runs of horizontal piping shall be grouped together on trapeze type hangers.  Vertical risers shall be supported at each floor line with approved steel pipe riser clamps.  The use of wire or perforated metal to support pipes will not be permitted.  Hanging pipes from other pipes shall not be permitted.  Spacing of pipe supports shall not exceed eight feet for pipes up to 1-1/4 inches and ten feet on all other piping.  Small vertical pipes (1 inch and less) shall be bracketed to walls, structural members, etc. at four (4) foot intervals so as to prevent vibration or damage by occupants.  Insulated piping shall be supported on a rigid insulation block at each hanger so as to prevent crushing of insulation by hangers.  Hangers shall pass completely around the insulation jacket and a steel protective saddle shall be applied to prevent compression of the insulation.  (Refer to Specifications Section entitled INSULATION-MECHANICAL).

  - Where piping rests directly on a hanger, clip, bracket or other means of support, the support element shall be of the same material as the pipe, (e.g., copper to copper, ferrous to ferrous, etc.) or shall be electrically isolated one from the other so as to prevent pipe damage by electrolysis.  Pay particular attention and do not allow copper pipe to rest on ferrous structural members, equipment, etc. without electrolytic isolation.

  - In general, piping shall be installed concealed except in Mechanical, Janitor Rooms, etc. unless otherwise indicated, and shall be installed underground or beneath concrete slabs only where indicated.  All lines at ceilings shall be held as high as possible and shall run so as to avoid conflicts with other trades, and to facilitate the Owner's use and maintenance.  Location of pipe in interior partitions shall be carefully coordinated with whoever will construct the partitions after the piping is in place. Where exposed risers occur they shall be kept as close to walls as possible.

  - Installation of pipe shall be in such a manner as to provide complete drainage of the system toward the source.  Drain valves shall be provided at all drainage points on pipes.  Drain valves shall be 1/2" size gate type with 3/4" hose thread end and vacuum breaker.  Label each drain valve.

  - All hot and cold water piping shall be kept a sufficient distance apart so as to prevent heat transfer between them.  Cold water piping shall also be kept apart from refrigerant hot gas lines.

  - Piping carrying water or other fluids subject to freezing shall not be installed in locations subject to freezing; if in doubt, consult Engineer.

  - Piping for all drainage systems shall be installed to permit flow, trapping, and venting in accord with current codes and sound practice.

  - All cast iron soil pipe and fittings shall be coated inside and out with coal tar varnish.

  - Non-metallic piping shall be installed in strict accordance with the manufacturer's instructions.  If no such instructions are available, consult Engineers.

  - Nipples shall be of the same material, composition and weight classification as pipe with which installed.

  - Where piping is not indicated on the plans, but is obviously or apparently required, contact the Engineers prior to submission of a bid proposal.

  - Pay particular attention to conflict of piping with other work.  Do not install until conflict is resolved.  If necessary, contact Engineers.

  - Piping materials in each system shall, to the extent practicable, be of the same material.  Frequent changes of material (for example, from copper to steel) shall be avoided and in no case shall be accomplished without use of insulating unions and permission of the Engineers.

  - Apply approved pipe dope (for service intended) to all male threaded joints.  Pay particular attention to dope for fuel gas lines. The dope shall be listed for such use.

  - High points of closed loop hot water heating systems shall have manual air vents as indicated or required unless automatic air vents are specifically indicated.  Pipe to suitable drainage point.

  - All piping shall be capped or plugged during erection as required to keep clean and debris and moisture free.

  - The entire domestic hot, cold and recirculating hot water piping system shall be sterilized in strict accord with requirements of the Department of Health Codes, Rules and Regulations for the State which the work is being accomplished in.

  - Provide expansion joints where shown on the plans and where required by good practice.  Expansion joints shall be guided and anchored in accordance with the recommendations of the Expansion Joint Manufacturer's Association.

  - Where plastic pipe penetrates a fire rated assembly, it shall be replaced with a metal threaded adapter and a metal pipe per code.

  - Where piping penetrates interior or exterior walls, the wall shall be sealed air tight.  Refer to the sleeving, cutting, patching and repairing section of the specifications for additional requirements.

  - Provide thrust blocks on all storm, sanitary, water, steam, hot, chilled , condenser, etc., and any other piping subject to hammering.  Thrust blocks shall be provided at all turns.

  - All piping to hydronic coils shall be full size all the way to the coil connection on the unit.  If control valve is smaller than pipe size indicated, transition immediately before and after control valve.  Also, if coil connection at unit is a different size than the branch pipe size indicated, provide transition at coil connection to unit. On 3-way valve applications, the coil bypass pipe shall be full size.

  - Provide check valves on individual hot and cold water supplies to each mixing valve (including each sensor style faucet, safety shower, etc.) and each showerhead with a diverter valve (including all ADA showers).

- UNIONS AND FLANGES AND WELDED TEES

  - Screwed unions, soldered unions or bolted flanges shall be provided as required to permit removal of equipment, valves and piping accessories from the piping system.  Keep adequate clearances for coil removal, rodding, tube replacement, motor lubrication, filter replacement, etc.  Flanged joints shall be assembled with appropriate flanges, gaskets and bolting.  Gaskets for steam piping systems shall be flexitalic spiral wound type.  The clearance between flange faces shall be such that the connections can be gasketed and bolted tight without imposing undue strain on the piping system.

  - Dielectric insulating unions or couplings shall be used wherever the adjoining materials being connected are of dissimilar metals such as connections between copper and steel pipe.

  - Tee connections for welded pipe shall be made up with welding fittings. Where the size of the side outlet is such that a different connection technique than on the run is required, a weldolet, sockolet, or threadolet type fitting may be used for the branch in place of reducing tees only where the branch is 2/3 the run size or smaller.

- SPECIFICATIONS STANDARDS

All piping and material shall be new, made in the United States and shall conform to the following minimum applicable standards:

  - Steel pipe; ASTM A-120, A-53 Grade A, A-53 Grade B.

  - Copper tube; Type K, L, M; ASTM B88-62; Type DWV ASTM B306-62.

  - Cast iron soil pipe; ASA A-40.l and CS 188-59.

  - Cast iron drainage fittings; ASA B16.12.

  - Cast iron screwed fittings; ASA B16.4.

  - Welding fittings; ASA B16.9.

  - Cast brass and wrought copper fittings; ASA B16.18.

  - Cast brass drainage fittings; ASA B16.23.

  - Reinforced concrete pipe; ASTM-C-76-64T.

  - Solder; Handy and Harmon, United Wire and Supply; Air Reduction Co. or equivalent.

  - CPVC Plastic pipe; ASTM D2846.

  - PVC plastic pipe; ASTM D1785.

- PITCH OF PIPING

All piping systems shall be installed so as to drain to a low point.  Certain minimum pitches shall be required for this drainage.  For proper flow and/or for proper operation, the following pitches shall be required:

  - Interior Soil, Waste and Vent Piping:

1/4 inch per foot in direction of flow where possible but in no case less than 1/8" per foot.

  - Roof Leaders:

1/8 inch per foot where possible.  Where not possible, run dead level.

  - Condensate Drain Lines From Cooling Equipment:

Not less than 1/4 inch per foot in direction of flow.

  - All Other Lines:

Provide ample pitch to a low point to allow 100 percent drainage of the system.

- APPLICATIONS

  - General Notes

    - Where plastic piping penetrates a fire rated assembly, it shall be replaced with a threaded metal adapter and metal pipe or whatever means necessary to maintain the separation rating in accordance with local plumbing and fire codes.

    - Plastic piping or any materials with a flame and smoke spread rating not approved for plenum use shall not be permitted in supply, return, relief or exhaust plenums.

    - PVC or plastic piping whether specifically listed or not may not be used in high rise buildings or anywhere else prohibited by code.

  - Fire Protection - Exterior and Interior

Refer to the Fire Protection System section of these specifications.

  - Soil Waste and Vent Piping - General Requirements

    - Water closet floor flanges and ells shall be cast iron regardless whether PVC piping is allowed or not.

    - Soil and waste piping serving mechanical rooms, shall be cast iron regardless whether PVC piping is allowed or not.  Cast iron will also be required at any other location where waste water temperature can exceed 120°F.  Cast iron shall extend a minimum of 35' past last waste inlet.

  - Soil, Waste and Vent Piping (Below Slab)

    - Schedule 40 PVC pipe with drainage pattern fittings and solvent cement joints made in accordance with the Kentucky Plumbing Code.

    - Service weight hubless cast iron with manufacturer's approved bands.

  - Soil, Waste and Vent Piping (Above Slab)

    - Service weight hubless cast iron pipe with manufacturer's approved bands.

    - Schedule 40 PVC pipe with drainage pattern fittings and solvent cement joints made in accordance with the Kentucky Plumbing code.

  - Roof Leaders/Interior Storm Sewer Piping

    - Service weight hubless cast iron pipe with manufacturers approved bands.

    - Schedule 40 PVC pipe with drainage pattern fittings and solvent cement joints.

  - Sump Pump Discharge

    - Type “M” copper with solder joints.

  - Natural Gas Piping – Interior

    - Schedule 40 black steel pipe with malleable iron threaded fittings for pipe sizes 2" and smaller.

    - Schedule 40 black steel pipe with wrought steel buttwelded fittings for pipe sizes 2-1/2" and larger.

NOTES:

(1)	All gas piping shall be installed per NFPA 54.

(2)	Unions or valves shall not be installed in an air plenum.

(3)	Piping below slab must be sleeved and vented.

(4)	Piping installed in concealed locations shall not have mechanical joints.

  - Domestic Cold, Hot and Recirculating Hot Water Piping (Above Slab)

    - Type "L" hard copper tubing with wrought copper fittings with lead free solder equivalent in performance to 95/5.  Lead free solder.

  - Domestic Cold, Hot and Recirculating Hot Water Piping (Below Slab)

Type "K" hard or soft copper tubing with wrought copper fittings and brazed joints.  There shall be no joints beneath slabs.

  - Hydronic Piping (Hot, Chilled)

    - 2" and Smaller:  Schedule 40 black steel pipe with screwed fittings or Type "L" hard copper tubing with wrought copper fittings and 95/5 solder.

    - 2-1/2" and Larger:  Schedule 40 black steel pipe with 125# welded or flanged joints.  Weldolets may be used for branch line connections to pipe mains.  Type "L" hard copper piping with wrought copper fittings and 95/5 solder may be installed.

    - Special Notes:

      - Dielectric unions shall be provided at all connections of dissimilar materials.

      - Copper and steel piping shall not be mixed in the mechanical room.

      - Takeoffs and branch piping to individual coils or heat pumps shall not be connected to the bottom of hydronic mains.  Connection to mains shall be at the side of the main.  Also refer to details on the drawings.

  - Air Vent Discharge Lines

Type "L" soft copper; wrought copper fittings, 95/5 solder.

  - Geothermal / Heat pump loop piping (Interior)

    - Mains– Piping shall be virgin polyethylene with a PE 3408 piping formaulation and 345464C or greater cell classification.  Pipe shall be SDR 15.5, minimum pressure rating of 110 psi at 73.4°F. Branches shall be copper.  Copper piping shall be insulated per Specifications.  All HDPE piping 3 inch and smaller shall be installed in a metal “V” channel with hangers intended for a “V” channel.

    - Transitions from polyethylene to copper – refer to detail on drawings.  Factory manufactured transition required with brass threads.  No metal threads shall be inserted into polyethylene piping, and no polyethylene threads shall be inserted into metal piping.

    - The only acceptable method for joining pipe is by a heat fusion process.  Pipe shall be butt or socket fused in accordance with pipe manufacturer's procedures.  Installers shall have heat fusion school certification per geothermal specifications.  Provide copy of heat fusion card to Engineer for review.

    - Special Notes:

      - Takeoffs and branch piping to individual coils or heat pumps shall not be connected to the bottom of hydronic mains.  Connection to mains shall be at the side of the main.  Also refer to details on the drawings.

  - Condensate Drain Lines

    - Type "DWV” copper, wrought copper, lead free solder.

    - Schedule 40 PVC with solvent welded fittings.

  - Water Heater Relief Line

Type "M" copper tubing with sweat fittings and 95/5 solder.

  - LP Gas Piping

Same as specified for natural gas piping.

END OF PIPES