SECTION 220100 - PLUMBING SPECIALTIES

- GENERAL

  - The Contractor's attention is directed to the General and Special Conditions, General Conditions-Mechanical and to all other Contract Documents as they apply to this branch of the work.  Attention is also directed to all other sections of the Contract Documents which affect the work specified in this section.

  - The Contractor shall provide all equipment and specialties complete with trim required and connect in a manner conforming to the Kentucky Building Code.

  - The Contractor shall obtain exact centerline rough-in dimensions between partitions, walls, etc. as required for lay-out of his rough-in work.  All work shall be roughed-in so that all exposed piping will be straight and true without bends or offsets.

  - Prior to final inspection, test by operation at least twice, all equipment.

  - Prior to final inspection, remove all stick-on labels, dirt, grease, other removable stampings, lettering, etc. from equipment and specialties and thoroughly clean same.

  - All equipment and specialties shall be installed as recommended by the manufacturer in a neat and workmanlike manner.  Unacceptable workmanship shall be removed and replaced at the installing Contractor's cost.

- DRAINAGE SPECIALTIES

  - GENERAL

    - Provide all drainage specialties indicated, specified and/or required to provide complete and acceptable removal of all storm, sanitary, waste, laboratory waste, etc. from the building and into approved receptors.

    - Drainage specialties shall be on non-electrolytic conduction to the material to which they are connected.

    - Drainage specialties shall be installed in a manner so as to insure no leakage of toxic or odorous gases or liquids and shall have traps and/or backflow preventers where required.  Nor shall they allow backflow into other or existing systems.

  - CLEANOUTS - INTERIOR (CO)

    - In addition to cleanouts indicated, provide cleanouts in soil and waste piping and storm drainage at the following minimum locations:

      - At base of each stack.

      - At fifty (50) foot maximum intervals in horizontal lines.

      - At each change of direction of a horizontal line.

      - As required by current KBC.

      - As required to permit rodding of entire system.  (If in doubt, contact Engineers.)

    - Water closets, slop sinks and other fixtures with fixed traps shall not be accepted as cleanouts.

    - Cleanouts and/or test tees concealed in inaccessible pipe spaces, walls and other locations shall have an eight (8) inch by eight (8) inch (minimum) access panel or cover plates shall be set flush with finished floors and walls and shall be key or screw driver operable.

    - Access panels for cleanouts shall be of the Zurn, 1460 series or equivalent by Josam or Watts.  Where they are not to receive paint, they shall be polished bronze unless otherwise indicated where they are to receive paint or other finishes.  They may, at the Contractor's option, be Perma-Coated steel, prepared to receive finish.

    - Cleanouts and access panels shall be sized so as to permit the entry of a full sized rodding head capable of one hundred percent circumferential coverage of the line served.

    - Provide a non-hardening mixture of graphite and grease on threads of all screwed cleanouts during installation.

    - Do not install cleanouts against walls, partitions, etc. where rodding will be difficult or impossible.  Extend past the obstruction.

    - In finished walls, floors, etc., insure that cleanouts are installed flush with finished surfaces and, where required, grout or otherwise finish in a neat and workmanlike manner.

    - Cleanouts shall be as manufactured by Zurn, Josam, Jay R. Smith, Watts, MIFAB, Ancon or equivalent, similar to the following:

      - Zurn, Z-1440 cleanouts or Z-1445 cleanout tee at base of exposed stack and at change in direction of exposed lines.

      - Zurn, Z-1440 cleanout or Z-1445-1 cleanout tee where stacks are concealed in finished walls

      - Zurn, ZN-1400-T cleanout with square scoriated top in finished concrete and masonry tile floors.

      - Zurn, ZN-1400-Tx cleanout with square recessed top for tile in vinyl and linoleum finished floors.

      - Zurn, ZN-1400-Z cleanout with round recessed top for terrazzo floors.

      - Zurn, Z-1400-HD cleanout with tractor cover for exterior locations.  Provide concrete supporting pad crowned to shed water.  Refer to drawings for pad size.

      - Mueller, No. D-731 or D-714, Nibco, Flage or equivalent for cleanouts in copper waste with cover plates and/or access panels listed for other cleanouts.

      - Threaded hex head type cleanouts of same materials as pipe for piping 2" and smaller.

      - Zurn, cleanout with round top with adjustable retainer for carpet area.  Install flush with carpet.

  - TRAP PRIMERS

Provide trap primers for all floor drains and open receptacle. Acceptable Trap Primer Manufacturers included Zurn, Precision Plumbing Products and Sioux Chief. Trap Primer selection shall be as follows:

    - Trap Primer Type-1 (TP-1)

Precisions Plumbing Products Prime-Time or equal electronic trap priming manifold, with atmospheric vacuum breaker, pre-set 24 hour clock, manual override switch, 120 volt solenoid valve with 120v/3wire connection.  Provide in 12” x 12” x 4” surface mounted metal cabinet.  Provide with 10 opening manifold, un-used manifold opening shall be capped.  Install united as required by manufacturer.

    - Trap Primer Type-2 (TP-2)

Precision plumbing products Prime-Rite or equal trap primer shall be installed on a cold water line, with distribution unit(s) to serve 1 to 8 drains.  Install per manufacturer’s recommendations.

    - Trap Primer Type-3 (TP-3)

Zurn Z-1022 or equal trap primer shall be installed in cold water supply line of nearest plumbing fixture.  One trap primer per floor drain, one trap primer per fixture.  Pipe to waste inlet per manufacturer’s recommendations.

- WATER SUPPLY SPECIALTIES

  - GENERAL

    - Provide all water supply specialties indicated, specified and/or required for the complete installation.  Install in a neat and workmanlike manner in accordance with the manufacturer's recommendations and the KBC.

    - Where required by the KBC, install code approved vacuum breakers in each water supply specialty.

  - FREEZEPROOF WALL HYDRANTS (FPWH)

    - Provide code approved wall hydrants at each location indicated in a neat and workmanlike manner.  Affix tight to walls and insure that the feed piping is on the heated side of the building insulation blanket.

    - Where hydrants are of handwheel type, remove handwheels and turn over to owners in an envelope labeled "Wall Hydrants" exterior upon completion of the project.

    - Where hydrants have key operators, turn over at least two (2) keys in an envelope labeled "Wall Hydrants" to owners upon completion of the project.

    - Where hydrants have lockable boxes, turn over at least two (2) keys in an envelope labeled "Wall Hydrants, Exterior" to owners upon completion of project.

    - Mount all wall hydrants at least twenty (20) inches above finished exterior grade.  Where this is not possible or practical, contact Engineers.

    - Wall hydrants shall be as follows or equivalent:

      - Zurn 1300 or equivalent, 3/4", encased, flush, non-freeze wall hydrant with key lock and combination backflow preventer/vacuum breaker.

  - HOSE BIBBS (HB)

    - Provide code approved hose bibbs with vacuum breakers and male threaded spouts at each location indicated and as follows:

    - Do not install hose bibbs spaces which do not have existing planned or installed floor drains even if sill cocks are indicated for these areas.

    - Hose bibbs shall be mounted at eighteen (18) inches above finished floor served.

    - The hose bibb shall be Woodford or equivalent similar to the following:

      - Woodford Model 24 with loose key handle polished chrome finish, brass construction.

  - BOILER DRAINS (BD)

Install 3/4 inch bronze body boiler drains, similar and equivalent to Nibco, No. 72 or 73, as indicated and at the following locations:

    - At the low point of the plumbing system.

    - On boiler low point.

    - In each hot water heater and/or storage tank.

    - At the low point of each hydronic system.

    - On the water refrigeration machine (100 percent drainage).

    - On each water storage tank.

    - At each pump suction.

    - At the low point of each isolatable section of any system carrying water.

NOTE:  Install a code approved vacuum breaker where installation on to domestic  water system.

  - WATER HAMMER ARRESTORS (WHA):  Provide water hammer arrestors at each location indicated and/or as required to eliminate hydrostatic on the domestic water system.  Provide at least one water hammer arrestor at all quick acting valve locations including:

Mop Basins (downstream of check valve) – Type “A”

Flush valve fixtures - Type “B” (Each toilet room with 1-3 flush valve fixtures shall have its own Type “B” water hammer arrestor.)

    - Multiple Fixtures – Branch Line Less Than 20’ Long:  The preferred location for a Zurn Shoktrol is at the end of the branch line between the last two fixtures when the branch lines do not exceed 20’ in length, from the start of the horizontal branch line to the last fixture supply on this line.

    - Multiple Fixtures – Branch Line More Than 20’ Long: On branch lines over 20’ in length, use two Shoktrols whose capacities total the requirement of the branch.  Locate one unit between the last and next to last fixture and the other unit approximately midway between the fixtures.

    - Water hammer arrestors shall be Zurn,  Z-1700, Shoktrol, Smith, Josam, Wade, or equivalent.  Water hammer arrestors shall be stainless steel, bellows type.  Field fabricated capped cylinders shall not  be acceptable.

    - Note: Provide insulation unions where arrestors are of dissimilar material from the piping served (unless piping is non-conducting, such as ABS or PVC).

| MARK | MANUFACTURER & MODEL | SIZE | P.D.I. SIZE |
| --- | --- | --- | --- |
| TYPE "A" | ZURN, Z-1700 # 100 | 1-11 | A |
| TYPE "B" | ZURN, Z-1700 # 200 | 12-32 | B |
| TYPE "C" | ZURN, Z-1700 # 300 | 33-60 | C |
| TYPE "D" | ZURN, Z-1700 # 400 | 61-113 | D |

  - PRESSURE REDUCING VALVES (PRV)

Install at each location indicated and/or as required to reduce domestic building water service to a maximum of eighty (80) PSIG code approved pressure reducing stations with by-pass.  Install in a manner indicated or as required.  Provide unions and stops for removal of station.  PRV shall be adjustable from thirty (30) percent above or below reduced pressure.   Where this cannot be attained with single stage, provide multiphased reduction.

  - REDUCED PRESSURE BACKFLOW PREVENTERS (RPBP)

Watts #909 or equivalent reduced pressure backflow preventer.  Provide with gate valves for isolation, strainer and air gap fitting.  RPBP shall be UL listed.

  - DOUBLE CHECK VALVE ASSEMBLY

Watts #709, Watts #757, or equivalent double check valve assembly.  Provide with strainer and gate valves for isolation.  Assembly shall be UL listed.

- GENERAL SPECIALTIES

  - VACUUM BREAKERS AND BACK FLOW PREVENTERS

Where required by the KBC, whether indicated or not, provide approved vacuum breakers or backflow preventers at the following locations.

    - Where domestic water system connects to fire protection system.

    - Where domestic water system connects to hydronic system.

    - At any hose (threaded) tap on the domestic water system.

  - ROOF FLASHINGS

All plumbing vents or other plumbing passing thru the roof shall be flashed as approved by the KBC and as recommended by the roofing manufacturer and/or Contractor.

  - GAS PRESSURE REGULATORS

Provide gas pressure regulators for all gas fired equipment that requires a lower pressure than what is delivered to the appliance. Regulators shall be installed in accordance with the requirements of NFPA 54 and/or International Fuel Gas Code, whichever is more stringent.

END OF PLUMBING SPECIALTIES