SECTION 200400 - DEMOLITION AND SALVAGE

- GENERAL

  - The Contractor's attention is directed to the General and Special Conditions, General Conditions-Mechanical and to all other Contract Documents as they apply to this branch of the work.  Attention is also directed to all other sections of the Contract Documents which affect the work of this section and which are hereby made a part of the work specified in this section.

- DEMOLITION

  - INTENT

It is the intent of this section to completely remove all components of any existing mechanical system no longer in use that will be open to view in, or will interfere with the operations of the completed building, or which will, in any way, interfere with project construction.  Components of the existing mechanical systems which do not meet the above criteria, may be abandoned in place in a safe, workmanlike, code approved manner.

  - PLUMBING

    - All existing piping not to be reused, shall be removed when located in accessible chases, accessible ceiling spaces, crawl spaces, mechanical rooms, exposed, etc.

    - Unless otherwise indicated, the Contractor shall be responsible for patching and repairing all holes, etc. in the ceilings, walls, and floors where plumbing piping is removed.

    - All lines abandoned in place shall be made safe in compliance with the Kentucky Plumbing Code.

  - HVAC

    - Remove from the project area all piping not to be reused and hangers, specialties, etc. that are accessible or that become accessible during construction and/or interfere in any way with any part of the construction or would be exposed in the completed building.

    - Remove all temperature controls and related items that are accessible or become accessible during construction.

    - Remove all existing heating and ventilating equipment not indicated to be reused from the building.

    - The Contractor shall be responsible for the removal and/or relocation of any HVAC piping, equipment, fittings, valves, etc. which may, in the course of construction, interfere with the installation of any new and/or relocated Architectural, Structural, Mechanical or Electrical Systems at no increase in the contract price.

    - Unless otherwise indicated, the Contractor shall be responsible for the patching and repairing of all holes, etc. in the ceiling, wall and floors where HVAC equipment is removed.

    - Unless otherwise noted, when removing equipment sitting on a concrete pad, also remove the concrete pad and patch and repair floor to match adjacent surfaces.

  - REFRIGERANT RECOVERY

    - The Contractor shall have a licensed refrigerant recovery technician evacuate all refrigerants from all refrigeration equipment being removed in accordance with EPA guidelines and regulations.  The Contractor shall take all necessary precautions to not accidentally vent refrigerants to the atmosphere.  The recovered refrigerant shall be offered to the Owner.  If the Owner refuses it then it becomes the property of the Contractor.

  - THERMOSTAT, THERMOMETER, AND MERCURY BEARING DEVICE DISPOSAL

    - The Contractor shall dispose of all mercury bearing materials in accordance with state and federal guidelines The Contractor shall take all necessary precautions to not accidentally allow mercury to be released from the device during demolition.

- SALVAGE

  - Components to be delivered to the owner shall be specifically identified by the owner’s representative prior to beginning the demolition.  These components shall include, but are not limited to the following:

    - Hydronic base mounted pump.

    - Trane chiller controls.

  - Other items become the property of the Contractor and are to be removed from the site.

END OF DEMOLITION AND SALVAGE