SECTION 220200 - PLUMBING FIXTURES, FITTINGS AND TRIM

- GENERAL

  - The Contractor's attention is directed to the General and Special Conditions, General Conditions-Mechanical and to all other Contract Documents as they apply to this branch of the work.  Attention is also directed to all other sections of the Contract Documents which affect the work of this section and which are hereby made a part of the work specified in this section.

  - The Contractor shall provide all fixtures complete with trim required and connect in a manner conforming to the State Plumbing Code.

  - The Contractor shall obtain exact centerline rough-in dimensions between partitions, walls, etc. as required for lay-out of his rough-in work.  All work shall be roughed-in so that all exposed piping will be straight and true without bends or offsets.

  - All exposed piping or in casework below sinks, stops, traps, tailpieces, etc., shall be code approved chrome plated brass unless otherwise indicated or specified.  Water supplies shall connect through walls with stops and chrome plated escutcheons with set screws.

  - All fittings, fixtures and trim shall be new unless otherwise indicated or specified.  They shall also be of equivalent quality, dimensions, material, etc. as those specified.

  - Handicapped fixtures shall be mounted as recommended by the KBC and ADA.  Flush valve handles shall be located on the open and/or accessible side of the ADA stall.

  - All fixtures shall be mounted as recommended by the manufacturer.  Fixtures shall be rigidly mounted to walls and floors.  Pay particular attention to flush valves and bracket concealed portion to building structure during rough-in.  Loose, shaky flush valves, lavatories, etc. shall not be acceptable.

  - Prior to final inspection open all faucets and allow to run for fifteen (15) minutes, then remove all faucet aerators and thoroughly clean until smooth flow is obtained.

  - Prior to final inspection, test by operation at least twice:

    - (Where applicable) adequate flow of hot and/or cold water at;

      - All Faucets

      - Flush Valves

      - Hose Bibbs

      - Sill Cocks

      - All Other Valved Hot and/or Cold Water Openings In the Plumbing System

    - All toilet seats

  - Prior to final inspection, remove all stick-on labels, dirt, grease, other removable stampings, lettering, etc. from plumbing fixtures and thoroughly clean same.

  - All sink and lavatory traps shall have screw in plugs in the bottom for ease of cleaning and have mechanical fittings for ease of removal.

  - All fixtures shall be set level and true and shall be grouted into finished walls, floors, etc. in a neat and workmanlike manner with an approved waterproof non-yellowing grout for such service.

  - Special Note for Handicap Grab Rails:  Coordinate top of shower valves, flush valves, flush tank, etc., with location of grab rails as shown on the architectural plans.  The Contractor shall install all items to allow for installation, removal and service without removal of the grab bar.

  - All exposed drain pipes and domestic water piping under handicap accessible sinks and lavatories shall be insulated in accordance with ADA requirements and shall have a vinyl plastic covering over all insulation.

  - The Contractor shall obtain a copy of the casework shop drawings and confirm sinks, faucets, gas turrets, etc., will fit in the space provided.  Additionally, in ADA applications with handicap sink base cabinets, the Contractor shall limit the total distance from the bottom of the sink to the bottom of the P-trap and coordinate waste pipe rough-in height to ensure the proper installation of the handicap sink base cabinet front closure panel.  The Contractor shall not order sinks until he confirms no conflicts occur and shall adjust sink sizes if required.  If the Contractor orders sinks, faucets, etc., that do not fit in the casework supplied, he shall replace them at no additional cost.

  - All lavatories, sinks, etc. shall be supplied with center rear drain outlets where necessary to avoid conflict with casework, handicapped kneeboards, etc.   If the Contractor orders sinks that do not fit in the casework supplied, he shall replace them at no additional cost.

  - All single supply faucets shall be provided with mechanical mixing valves unless otherwise noted.  Mechanical mixing valves shall have hot and cold water inlet connections, common outlet, in-line check valves, and adjustable temperature setting.  Mixing valves shall be Moen model 104424 or equal.  Provide one mixing valve per single supply faucet unless otherwise noted.  Contractor shall provide all required connections and set mixing valve to required temperature.

- FIXTURES AND TRIM

Available Manufacturers:  Subject to compliance with requirements of manufacturers offering plumbing fixtures and trim.  Plumbing fixtures and trim, which may be incorporated in the work include, but are not limited to, the following:

  - Plumbing Fixtures - Water Closet, Lavatory, and Urinal

American Standard, U.S. Plumbing Products

Eljer Plumbingware Div., Wallace-Murray Corp.

Kohler Co.

Crane Plumbing

Toto

Zurn Co.

Sloan Fixtures

  - Plumbing Trim

American Standard, U.S. Plumbing Products

Chicago Faucet Co.

Kohler Co.

Delta Co.

T&S Brass & Bronze Work Co.

Zurn Co.

Just Co.

Speakman Co.

Moen Commercial

  - Flush Valves

Delany Co.

Sloan Valve Co.

Zurn Co.

  - Fixture Seats

Bemis Mfg. Co.

Church Seat Co.

Olsonite Corp., Olsonite Seats

  - Water Coolers

Elkay Mfg. Co.

Halsey Taylor Div., King-Sealey Thermos Co.

Haws Drinking Faucet Co.

Western Drinking Fountains, Div. of Sunroc Corp.

Oasis Co.

Acorn AQUA

* Acceptable wall hung water coolers shall be equal to Oasis P8AM, Elkay EZS8 or Halsey Taylor  HAC8FS. All other wall hung water coolers shall be subject to review of the Engineer.

  - Service Sinks and Mop Basins

American Standard, U.S. Plumbing Products

Eljer Plumbingware Div., Wallace-Murray Corp.

Fiat Products

Kohler Co.

Stern-Williams Co., Inc.

Florestone

  - Stainless Steel Sink

Elkay Mfg. Co.

Just Mfg. Co.

Moen, Div. of Stanadyne/Western

Sterling Co.

  - Fixture Carriers

Josam Mfg. Co.

Jay R. Smith

Tyler Pipe

Zurn Industries

Watts

Guardian Co.

  - P-Trap Insulation Kit (Trap Wrap)

Truebro

Brocar

Plumberex

Note:	Kitchen, Special Equipment, Etc.

Contractor to provide final plumbing connections to all of the equipment furnished by Owner including, but not limited to:  chrome supplies, stops, continuous drains, drain tailpiece, Kentucky Code "P" traps and escutcheons.

- FIXTURE SELECTION

  - Refer to drawings for fixture schedule.

END OF PLUMBING FIXTURES