SECTION 202110 - ACCESS TO VALVES, EQUIPMENT, FILTERS, ETC.

- GENERAL

  - The Contractor's attention is directed to the General and Special Conditions, General Requirements-Mechanical and to all other Contract Documents as they apply to this branch of the work.  Attention is also directed to all other sections of the Contract Documents which affect the work of this section and which are hereby made a part of the work specified herein.

  - All mechanical equipment shall be installed in a manner which allows ready access to all components requiring service, adjustments, shutoff, etc.

  - Filters shall be accessible, removable and replaceable without disconnecting mounting brackets, piping, wiring, etc.

  - All oil cups, grease cups, grease fittings, etc. shall be accessible without disassembly of equipment, piping, ductwork, etc.  (Extended oilers or grease fittings may be required).

  - Provide access doors or panels for all equipment, valves, dampers, filters, fire dampers, etc. in concealed spaces not otherwise provided with suitable access.  (Lay-in ceilings shall be considered acceptable access; splined or drywall ceilings shall not).

  - All valves, unions, strainers, cleanouts, and test points shall be accessible.

  - Access panels in lay-in ceilings shall be marked with colored tacks to indicate location of equipment, filters, valves, etc.

  - Access panels in fire rated walls shall bear the same rating as the wall.

  - Each fire damper shall be provided access through the duct to allow reset of the damper.  This may be either a gasketed sheet metal panel over a suitable opening or a factory built access panel.  The panel shall be at least one and one-half (1) inch larger than the opening all around and shall be held in place with sheet metal screws sufficiently to insure that it is air tight.  Manually check the size and location of each of these openings to insure that the fire damper may be manually reset by use of hand only.

- ACCESS DOORS

Refer to Sheet Metal and Flexible Duct section of the specifications.

END OF ACCESS TO VALVES AND COCKS