SECTION 250200 - CONTROLS – DIRECT DIGITAL

- GENERAL

  - The Contractor shall furnish all labor, materials, equipment and services required to provide a complete Web based temperature control system as specified and as shown on the plans.

  - Prior to the installation of or payment for any work, the Contractor shall prepare submittals which shall be reviewed by the Architect and Engineer.  These submittals shall include a complete control diagram and sequence of operation of the entire system, plus engineering data on all devices used.

  - The system herein specified shall be free from defects in workmanship and material under normal use and service if, within twelve (12) months from the date of acceptance by the Engineer, any of the equipment herein described is proved to be defective in workmanship or material, it will be adjusted, repaired, or replaced free of charge by the Contractor.

  - All equipment, unless specified to the contrary, shall be fully proportioning and adjustable.  The Control System shall consist of all room thermostats, air stream thermostats, valves, damper operators, relays, freeze protection equipment, dampers, panels, and other accessory equipment not provided with the equipment to fill the intent of the specifications and drawings.

  - All units, controls, equipment, heat pumps, etc., and controls shall reset automatically when power is restored after an outage.

  - All control wiring concealed in walls and exposed in mechanical rooms, closets, etc., shall be in conduit.  Provide plenum rated wiring where cable is concealed above ceilings.  Do not paint wiring.  The Contractor is responsible for protecting wiring from paint.  Any painted cabling shall be replaced.

  - All dampers shall be capable of operating properly with the system pressures encountered.  This shall include modulating and shut-off functions.

  - The Contractor shall also refer to the mechanical maintenance, HVAC equipment, and all other sections of the specifications for additional control requirements.

  - Provide smoke detectors and shut down control for all air handling units and combined air systems as required by the KBC and IMC Section 606.

  - All DDC controllers or control modules shall have covers to protect the circuit boards.  All wiring shall be anchored securely within 6" of the controller.

  - Provide all control dampers, etc. not supplied with the equipment or required to accomplish the sequences specified.

  - The Contractor shall provide all refrigeration control and interlock wiring as recommended by the equipment manufacturer.

  - Wiring and required conduit in connection with the control system(s), including power wiring of any voltage, shall be installed by the Contractor.  The Contractor may, at his option, engage the Electrical Contractor to accomplish this work.  It is emphasized however, that the Contractor is finally responsible for all such work.

  - Electric power for the control panels, modules, unit controller, damper motors, etc., shall be derived from the building electric system.  Power shall not be derived from the HVAC equipment power source or equipment low voltage transformers (internal or integral).

  - The electrical work required for the installation of the control system(s), shall be provided by the Contractor in accordance with all National and Local Electrical Codes.  All wiring shall be concealed except in Mechanical Rooms.  All electrical work specified under this division of the specifications shall also comply with Division 26 of these specifications.

  - All exterior electrical work, equipment, etc. shall be waterproofed.

  - Controls system and all related components shall comply with ASHRAE Standard 135 (BACnet protocol).

  - The Contractor shall provide full instructions to designated personnel in the operation, maintenance, and programming of the system per Specification 017900. Eight hours of Owner Training shall be provided at substantial completion, again after 6 months (four hours) and (four hours) again 1 year after substantial completion.

- CONTROL SYSTEM CHECKOUT AND TESTING – BY CONTROLS CONTRACTOR PRIOR TO DEMONSTRATION AND ACCEPTANCE

  - Startup Testing.  Complete startup testing to verify operational control system before notifying Owner of system demonstration.  Provide Owner with schedule for startup testing.  Owner may have representative present during any of all startup testing.

- Calibrate and prepare for service each instrument, control, and accessory equipment furnished under Section 250200.

- Verify that control wiring is properly connected and free of shorts and ground faults.

- Enable control systems and verify each input device’s calibration.  Calibrate each device according to manufacturer’s recommendations.

- Verify that binary output devices such as relays, solenoid valves, two-position actuators and control valves, and magnetic starters, operate properly and that normal positions are correct.

- Verify that analog output devices such as I/Ps and actuators are functional, that start and span are correct, and that direction and normal positions are correct.  Check control valves and automatic dampers to ensure proper action and closure.  Make necessary adjustments to valve stem and damper blade travel.

- Prepare a log documenting startup testing of each input and output device, with technician’s initials certifying each device has been tested and calibrated. Submit log to Engineer for review.

- Verify that system operates according to sequences of operation.  Simulate and observe each operational mode by overriding and varying inputs and schedules.  Tune PID loops and each control routine that requires tuning.

- Alarms and Interlocks.

  - Check each alarm with an appropriate signal at a value that will trip the alarm.

  - Trip interlocks using field contacts to check logic and to ensure that actuators fail in the proper direction.

  - Test interlock actions by simulating alarm conditions to check initiating value of variable and interlock action.

- PREPARATION AND COORDINATION

  - Coordination Meeting

The BMS installer and the Mechanical Engineer shall hold an onsite meeting with the State Project Manager, DECA representative, Engineer, Contractor and Mechanical Contractor onsite.  This meeting shall occur by 70% project Construction completion.

  - TAB coordination

The Building Automation System (BAS – Controls) Contractor will provide to the Testing and Balance (TAB) Agency temporary use of a computer, software and other BAS related equipment needed to properly balance the systems and perform related work.  The BAS Contractor will also instruct the TAB Agency on proper operation of the BAS systems, if requested.  In the event the main computer is not located in the construction area, the BAS Contractor has the option to provide a technician or a suitable portable computer for the use of the TAB Agency.  Upon completion, all computers and equipment will be returned to the BAS Contractor.

- ONSITE RESPONSIBILITY

  - Project Management Services: The building automation contractor shall have a project manager assigned to this project and shall attend all pre-construction and construction progress meetings.  The project manager shall supervise the installation of the complete temperature control system and shall be available to the mechanical contractor to answer any questions related to the installation and operation of the water source heat pumps, 100% outside air units with energy recovery, and temperature control system.

  - The Owner shall sign a copy of the manufacturer’s standard software and firmware licensing agreement as a condition of this contract. All software licensing shall be made to the Owner not the BMS Contractor or vendor, and such license shall grant use of all programs and application software to owner as defined by the manufacturer’s license agreement, but shall protect manufacturer’s rights to disclosure of trade secrets contained within such software. All software shall be capable of adding other manufacture licensed vendors if of the same firmware. All project developed software, control software and documentation shall become the property of the owner. These include, but are not limited to project graphic images, record drawings, project database, project specific application programming code, and all other associated documentation. Any and all required IDs, passwords, and software keys for access to any component or software program shall be provided to the owner.   The OWNER shall receive a CD with O&M’s that include all necessary software, sequences, programming, etc to reinstall the BMS if a system should fail.

  - All project developed hardware and software shall become the property of the Owner.  These include but are not limited to:

  - Project graphic images,

  - Record drawings,

  - Project database,

  - Job-specific application programming code.

  - All software, software licenses and software keys.

  - All documentation.

- QUALITY ASSURANCE

A.	The BMS herein specified shall be fully integrated and installed as a complete package by the BMS Contractor. The System shall include all wiring, piping, installation supervision, calibration, adjustments, and checkout necessary for a complete and fully operational system. Work shall be installed under the supervision of a project manager with a minimum of 10 years experience.

B.	Qualified Contractors:

Contractors shall be subject to full compliance with the requirements of the Drawings, sequences of operation, points lists and specifications.  The interested contractor shall document a minimum of 5 years experience with the complete, turnkey installation of the controls system they intend to install.

| Contractor | Manufacturer |
| --- | --- |
| Harshaw Trane | Trane |
| Innerspace | Automated Logic |
| JCI Branch Office | Johnson Controls |

C.	The BMS Contractor shall coordinate with other Trade Contractors regarding the location and size of pipes, equipment, fixtures, conduit, ducts, openings, switches, outlets, and so forth, in order to eliminate any delays in the progress of the job.

- SUBMITTALS

Contractor shall provide shop drawings and manufacturers’ standard specification data sheets on all hardware and software to be provided.  No work may begin on any segment of this project until the Engineer and Owner have reviewed submittals for conformity with the plan and specifications. Twelve (12) copies are required.  All shop drawings shall be provided to the Owner electronically as .dwg or .dxf file formats.

Quantities of items submitted shall be reviewed by the Engineer and Owner.  Such review shall not relieve the contractor from furnishing quantities required for completion.

Provide the Engineer and Owner, any additional information or data that is deemed necessary to determine compliance with these specifications or which is deemed valuable in documenting the system to be installed.

Submit the following within 60 days of contract award:

- A complete bill of materials of equipment to be used indicating quantity, manufacturer and model number.

- A schedule of all control valves including the valve size, model number (including pattern and connections), flow, CV, pressure rating, and location.

- A schedule of all control dampers.  This shall include the damper size, pressure drop, manufacturer and model number.

- Provide manufacturers cut sheets for major system components. When manufacturer's cut sheets apply to a product series rather than a specific product, the data specifically applicable to the project shall be highlighted or clearly indicated by other means. Each submitted piece of literature and drawings shall clearly reference the specification and/or drawing that the submittal is being submitted to cover.  Include:

- Building Controllers

- Custom Application Controllers

- Application Specific Controllers

- Operator Interface Computer

- Portable Operator Workstation

- Auxiliary Control Devices

- Proposed control system riser diagram showing system configuration, device locations, addresses, and cabling.

- Detailed termination drawings showing all required field and factory terminations.  Terminal numbers shall be clearly labeled.

- Points list showing all system objects, and the proposed English language object names.

- Sequence of operations for each system under control.  This sequence shall be specific for the use of the Control System being provided for this project.

- Provide a BACnet Product Implementation Conformance Statement (PICS) for each BACnet device type in the submittal.

- Color prints of proposed graphics with a list of points for display.

Project Record Documents: Upon completion of installation submit twelve (12) copies of record (as-built) documents.  The documents shall be submitted for approval prior to final completion and include:

- Project Record Drawings - These shall be as-built versions of the submittal shop drawings.  One set of electronic media including CAD .DWG or .DXF drawing files shall also be provided.

- Testing and Commissioning Reports and Checklists.

- Operating and Maintenance (O & M) Manual - These shall be as built versions of the submittal product data.  In addition to that required for the submittals, the O & M manual shall include:

- Names, address and 24-hour telephone numbers of Contractors installing equipment, and the control systems and service representative of each.

- Operators Manual with procedures of operating the control systems including logging on/off, alarm handling, producing point reports, trending data, overriding computer control, and changing set points and other variables.

- Programming Manual with a description of the programming language including syntax, statement descriptions including algorithms and calculations used, point database creation and modification, program creation and modification, and use of the editor.

- Engineering, Installation and Maintenance Manual(s) that explains how to design and install new points, panels, and other hardware; preventative maintenance and calibration procedures; how to debug hardware problems; and how to repair or replace hardware.

- A listing and documentation of all custom software created using the programming language including the point database.  One set of magnetic media containing files of the software and database shall also be provided.

- One set of electronic media containing files of all color-graphic screens created for the project, all sequences, programming, and software required to reinstall the system.

- A list of recommended spare parts with part numbers and supplier.

- Complete original issue documentation, installation, and maintenance information for all third party hardware provided including computer equipment and sensors.

- Complete original issue media for all software provided including operating systems, programming language, operator workstation software, and graphics software.

- Licenses, Guarantee, and Warrantee documents for all equipment and systems.

- Recommended preventive maintenance procedures for all system components including a schedule of tasks (inspection, cleaning, calibration, etc.) time between tasks, and task descriptions.

- WARRANTY

- Warrant all work as follows:

- Labor & materials for control system specified shall be warranted free from defects for a period of twelve (12) months after Substantial Completion.  Final acceptance by the Owner shall occur before Substantial Completion is achieved.  Control System failures during the warranty period shall be adjusted, repaired, or replaced at no charge or reduction in service to the Owner.  The Contractor shall respond to the Owner's request for warranty service within 24 hours during customary business hours.

- At the end of the final start-up/testing, if equipment and systems are operating satisfactorily to the Owner and Engineer, the Owner shall sign certificates certifying that the control system's operation has been tested and accepted in accordance with the terms of this specification.  The date of Owner's acceptance shall be the start of warranty.

- Operator workstation software, project specific software, graphics, database, and firmware updates shall be provided to the Owner at no charge during the warranty period.  Written authorization by Owner must, however, be granted prior to the installation of such changes.

- The system provider shall provide a web-accessible Users Network to give the Owner access to question/answer forum, graphics library, user tips, upgrades, and training schedules.

- CEMCS COMPLIANCE

  - This project shall satisfy all CEMCS naming and graphic requirements.  The Contractor shall review the latest CEMCS standards prior to submittal of Shop Drawings.  At this time, the BMS will not be monitored by CEMCS.  If the Contractor shall be provided with a copy of CEMCS standards upon request if they are not familiar with the document.

CEMCS Data Transfer  Connectivity Link between the Front End (Level 3) and the Commonwealth

Office of Technology (COT) database server.  Point Data shall be transferred in SQL Tables to a COT

database dedicated to each control system provide

Level 3 BAS network these connections shall be robust high speed hardware data links like Ethernet

using TCP/IP open standard connections.  Data on these networks shall run at PC Speeds with virtually no bandwidth restrictions.

For security reasons, it is best that BAS embedded servers provide or serve up data to COT servers.  COT best practices security policies state that when connecting servers to the Central FAC database that the most secure connection is when COT is pulling data. In CEMCS, COT servers will pull data at night

when network activity is minimal.

CEMCS Point Nomenclature   Each point of control shall be identified with a unique point name consistent with the KY/CEMCS I/O Standard Tag Identification format. This format consist of a multi-component point naming system including:

        - KY Archibus Building ID #

        - Building Area

        - Disclipline

        - Drawing Layer Group

        - Drawing Layer Sub-Group

        - System Component ID

        - I/O Point Descriptive Abbreviation

        - I/O Point Unique ID #

  - Sample Naming Nomenclature

    - Equipment Tagging

      - BBR- Baseboard Heater

      - CP- Control Panel

      - CUH- Cabinet Unit Heater

      - DWH- DWH

      - DWR- Domestic Water Return

      - HWS- Hot Water Supply

      - HWR- Hot Water Return

- PRODUCTS

- COMMUNICATION

- This project shall comprise of a network utilizing high-speed BACnet over IP communications between the Central Server, Building Controllers and the Operator PC Workstations

- LonTalk™, BACnet/mstp, or Zigbee Certified sub-networks shall be used for communications between Building Controllers, Custom Application Controllers and Application Specific Controllers.

- All Building Controllers shall have a communications port to allow for communications with other building controllers, service software PCs, and the centralized server. The connection shall be an Ethernet network interface node. Service software connections at a building controller may be optionally provided through an RS-232 port for Point to Point connection.

- Operator Interface

- The operator interface shall reside on a server and be accessible via a aeb browser.

- The operator interface shall support the following Internet web browsers:

- Internet explorer 8.0+

- Firefox 18.0+

- Chrome 24.0+

- The operator interface shall support the following mobile web browsers:

- iOS (iPad/iPhone)v4.0+

- Android (tablet) v4.0+

- Android (phone) v2.3+

- The central server shall consist of the following (minimum):

- System shall utilize a server class PC, tower or rack mounted

- Two Xeon 2.8 GHz, 1MB L3 cache processors

- 2GB, DDR 266 SDRAM memory

- Four (4) 72 GB SCSI HD (each) in RAID 5 or RAID 10 configuration

- DVD+R/W or CD ROM

- Microsoft Windows Server 2003 (IIS6.0)

- Microsoft SQL Servre 2005

- .NET Framework 1.1

- Furnish all required serial, parallel, and network communication ports, and all cables for proper system operation.  The server shall include a minimum 17", color monitor with 1024 X 768 screen resolution.

- The operator interface shall support the following mobile web browsers:

- Ios (ipad/iphone) v4.0+

- Android (tablet) v4.0+

- Android (phone) v2.3+

- The operator interface shall be accessible via a web browser.

- The operator interface shall support the following internet web browsers:

- Internet explorer 8.0+

- Firefox 18.0+

- Chrome 24.0+

- The operator interface shall support the following mobile web browsers:

- Ios (ipad/iphone) v4.0+

- Android (tablet) v4.0+

- Android (phone) v2.3+

- Mobile app operator interface

- Mobile app operator interface shall support the following operating systems

- Apple ios 5

- Apple ios 6

- Android v2.3

- Android v4.0

- Android v4.1

- The operator interface shall support system access on a mobile device via a mobile app to:

- Alarm log

- System status

- Equipment status

- Space status

- Standard equipment graphics

- The operator interface shall support actions on a mobile device via a mobile app to:

- Override set points

- Override occupancy

- Acknowledge alarms

- Comment on alarms

- System Security

- Each operator shall be required to login to the system with a user name and password in order to view, edit, add, or delete data.

- User profiles shall restrict the user to only the objects, applications, and system functions as assigned by the system administrator.

- Each operator shall be allowed to change their user password

- The system administrator shall be able to manage the security for all other users

- The system shall include pre-defined “roles” that allow a system administrator to quickly assign permissions to a user.

- User logon/logoff attempts shall be recorded.

- The system shall protect itself from unauthorized use by automatically logging off following the last keystroke.  The delay time shall be user definable.

- All system security data shall be stored in an encrypted format.

- Database

- Database save. A system operator with the proper password clearance shall be able to archive the database on the designated operator interface pc.

- Database restore.  The system operator shall also be able to clear a panel database and manually initiate a download of a specified database to any panel in the system.

- On-line help

- Provide a context sensitive, on line help system to assist the operator in operation and configuration of the system.

- On-line help shall be available for all system functions and shall provide the relevant data for each particular screen.

- System diagnostics

- The system shall automatically monitor the operation of all network connections, building management panels, and controllers.

- The failure of any device shall be annunciated to the operators.

- Equipment & application pages

- The operator interface shall include standard pages for all equipment and applications.  These pages shall allow an operator to obtain information relevant to the operation of the equipment and/or application, including:

- Animated equipment graphics for each major piece of equipment and floor plan in the system.  This includes: wshps, doas, pump, etc

- Animation capabilities shall include the ability to show a sequence of images reflecting the position of analog outputs, such as valve or damper positions. Graphics shall be capable of launching other web pages.

- Alarms relevant to the equipment or application without requiring a user to navigate to an alarm page and perform a filter.

- Historical data (as defined in automatic trend log section below) for the equipment or application without requiring a user to navigate to a data log page and perform a filter.

- System graphics

- Operator interface shall be graphically based and shall include at least one graphic per piece of equipment or occupied zone, graphics for each chilled water and hot water system, and graphics that summarize conditions on each floor of each building included in this contract.

- Graphics shall allow operator to monitor system status, to view a summary of the most important data for each controlled zone or piece of equipment, to use point and-click navigation between zones or equipment, and to edit set points and other specified parameters.

- Graphics shall use 3d images for all standard and custom graphics.  The only allowable exceptions will be photo images of the building as the home screen. All floor plans shall be drawn in 3-d and reflect that as built drawings. The engineer will provide dwg files of the final floor plan.

- Manual Control and Override.

- Point control.  Provide a method for a user to view, override, and edit if applicable, the status of any object and property in the system.  The point status shall be available by menu, on graphics or through custom programs.

- Temporary overrides.  The user shall be able to perform a temporary override wherever an override is allowed, automatically removing the override after a specified period of time.

- Override owners.  The system shall convey to the user the owner of each override for all priorities that an override exists.

- Provide a specific icon to show timed override or operator override, when a point, unit controller or application has been overridden manually.

- Scheduling.  A user shall be able to perform the following tasks utilizing the operator interface:

- Create a new schedule, defining the default values, events and membership.

- Create exceptions to a schedule for any given day.

- Apply an exception that spans a single day or multiple days.

- View a schedule by day, week and month.

- Exception schedules and holidays shall be shown clearly on the calendar.

- Modify the schedule events, members and exceptions.

- Trend logs

- Trend logs definition.

- The operator interface shall allow a user with the appropriate security permissions to define a trend log for any data in the system.

- The operator interface shall allow a user to define any trend log options as described in the application and control software section.

- The operator shall be able to define a trend log for any data in the system.  This definition shall include interval, start-time, and stop-time.  Trend intervals of 1,5,15, 30, and 60 minutes as well as user-defined intervals shall be selectable.  The system operator shall be able to determine how many samples are stored in each trend.  Trend data shall be sampled and stored on the Building Controller panel, then harvested and be archived on the central server hard disk.  Additionally, provide the capability to sample directly from the building controller database to the central server.  Trend data shall be able to be viewed and printed from the operator interface web pages.  Trends must be viewable in a text-based format or graphically.  Trends shall also be storage in a tab delimited ASCII format for use by other industry standard word processing and spreadsheet packages, and be exportable to a file for use in other software tools, available in a non-proprietary file format to be used by another database.

- Dynamic Graphical Trending.  The system shall have the ability to display collected data in a graphical chart.  Trend viewing capabilities shall include the ability to show up to 5 points on a chart.  Each data point trend line shall be an individual color.  Trend data shall be able to be stored indefinitely on the central server storage capacity and data archiving practices.

- Export trend logs.

- The operator interface shall allow a user to export trend log data in csv or pdf format for use by other industry standard word processing and spreadsheet packages.

- Alarm/Event Notification

- An operator shall be notified of new alarms/events as they occur while navigating through any part of the system via an alarm icon.

- Alarm/event log.  The operator shall be able to view all logged system alarms/events from any operator interface.

- The operator shall be able to sort and filter alarms from events. Alarms shall be sorted in a minimum of 4 categories based on severity.  The Owner shall be able to adjust the settings indicating which level alarms trigger remote notification.

- Alarm/event messages shall use full language, easily recognized descriptors.

- An operator with the proper security level may acknowledge and clear alarms/events.

- All alarms/events that have not been cleared by the operator shall be stored by the building controller.

- The alarm/event log shall include a comment field for each alarm/event that allows a user to add specific comments associated with any alarm.

- Alarm processing.

- The operator shall be able to configure any object in the system to generate an alarm when transitioning in and out of a normal state.

- The operator shall be able to configure the alarm limits, warning limits, states, and reactions for each object in the system.

- Reports and logs

- The operator interface shall provide a reporting package that allows the operator to select reports.

- The operator interface shall provide the ability to schedule reports to run at specified intervals of time.

- The operator interface shall allow a user to export reports and logs from the building controller in a format that is readily accessible by other standard software applications including spreadsheets and word processing. Acceptable formats include:

- Csv, html, xml, pdf

- Reports and logs shall be readily printed to the system printer.

- Provide a means to list and access the last 10 reports viewed by the user.

- The following standard reports shall be available without requiring a user to manually configure the report:

- All points in alarm report: provide an on demand report showing all current alarms.

- All points in override report: provide an on demand report showing all overrides in effect.

- Commissioning report: provide a one-time report that lists all equipment with the unit configuration and present operation.

- Points report: provide a report that lists the current value of all points

- Ashrae standard 147 report: provide a daily report that shows the operating condition of each chiller as required by ashrae standard 147.  At minimum this report shall include:

- APPLICATION AND CONTROL SOFTWARE

- Furnish the following applications software for building and energy management. All software applications shall reside and run in the system controllers.  Editing of applications shall occur at operator workstations served web-based user interface pages.

- Scheduling.  Provide the capability to schedule each object or group of objects in the system. Each of these schedules shall include the capability for start, stop, and optimal start actions.  When a group of objects are scheduled together, provide the capability to define advances and delays for each member.

- Optimal Start.  The scheduling application shall support an optimal start algorithm.  This shall calculate the thermal characteristics of a zone and start the equipment prior to occupancy to achieve the desired space temperature at the specified occupancy time.  The algorithm shall calculate separate sets of heating and cooling rates for zones that have been unoccupied for less than and greater than 24 hours.  Provide the ability to modify the start algorithm based on outdoor air temperature.  Provide an early start limit in minutes to prevent the system from starting before an operator determined time limit.

- Maintenance Management. The system shall monitor equipment status and generate maintenance messages based upon user designated run time, starts, and/or calendar date limits.

- PID Control.  A PID (proportional-integral-derivative) algorithm with direct or reverse action and anti-wind-up shall be supplied. The algorithm shall calculate a time-varying analog value used to position an output or stage a series of outputs. The controlled variable, set-point, and PID gains shall be user-selectable.  The setpoint shall optionally be chosen to be a reset schedule.

- Timed Override.  A standard application shall be utilized to enable/disable temperature control when a user selects on/cancel at the zone sensor, workstation, or the operator display.  The amount of time that the override takes precedence will be selectable from the workstation.

- Staggered Start.  This application shall prevent all controlled equipment from simultaneously restarting after a power outage.  The order in which equipment (or groups of equipment) is started, along with the time delay between starts shall be user-selectable.

- Anti-Short Cycling.  All binary output points shall be protected from short cycling. This feature shall allow minimum on-time and off-time to be selected.

- system CONTROLLERS

- There shall be one or more independent, standalone microprocessor based System Controllers to manage the global strategies described in Application and Control Software section.

#### The system controller shall have sufficient memory to support its operating system, database, and programming requirements.

#### The controller shall provide a usb communications port for connection to a pc

#### The operating system of the controller shall manage the input and output communications signals to allow distributed controllers to share real and virtual point information and allow central monitoring and alarms.

#### All system controllers shall have a real time clock.

#### Data shall be shared between networked system controllers.

#### The system controller shall continually check the status of its processor and memory circuits.  If an abnormal operation is detected, the controller shall:

- Assume a predetermined failure mode.

- Generate an alarm notification.

- Create a retrievable file of the state of all applicable memory locations at the time of the failure.

- Automatically reset the System Controller to return to a normal operating mode.

#### Environment.  Controller hardware shall be suitable for the anticipated ambient conditions. Controller used in conditioned ambient shall be mounted in an enclosure, and shall be rated for operation at -40 c to 50 c [-40 f to 122 f].

#### Clock synchronization.

- All System Controllers shall be able to synchronize with a NTP server for automatic time synchronization.

- All System Controllers shall be able to accept a bacnet time synchronization command for automatic time synchronization.

- All System Controllers shall automatically adjust for daylight savings time if applicable.

#### Serviceability

- Provide diagnostic leds for power, communications, and processor.

- The System Controller shall have a display on the main board that indicates the current operating mode of the controller.

- All wiring connections shall be made to field removable, modular terminal connectors.

- The System controller shall utilize standard DIN mounting methods for installation and replacement.

#### Memory.  The system controller shall maintain all bios and programming information indefinitely without power to the system controller

#### Immunity to power and noise.  Controller shall be able to operate at 90% to 110% of nominal voltage rating and shall perform an orderly shut-down below 80% nominal voltage

#### Environment.  Controller hardware shall be suitable for the anticipated ambient conditions. Controller used in conditioned ambient shall be mounted in an enclosure, and shall be rated for operation at -40 c to 50 c [-40 f to 122 f].

- All communication between the system controller and unit controllers (both application specific and custom) shall utilize lontalk, bacnet, or Zigbee certified communication standards. Controllers using Zigbee communication shall conform to the following:

    - IEEE 802.15.4 radios to minimize risk of interference and maximize battery life, reliability, and range.

    - Operating range shall be a minimum of 200 feet; open range shall be 2,500 ft. (762 m) with less than 2% packet error rate.

    - To maintain robust communication, mesh networking and two-way communications shall be used to optimize the wireless network health.

    - Certifications shall include FCC CFR47 - RADIO FREQUENCY DEVICES - Section 15.247 & Subpart E

    - Shall be ZigBee Building Automation Certified to allow wireless integration with products from multiple suppliers.

    - Wireless Comm Interface certifications shall include:

      - TFP-13651127 - Canada Compliance

      - UL 916 - Energy Management Equipment

      - UL 94 - The Standard for Flammability of Plastic Materials for Parts in Devices and Appliances: 5 VA flammability rating

      - UL 873 - Temperature regulating and indicating equipment

      - ZigBee Building Automation, BACnet Tunnelling Device

- CUSTOM APPLICATION CONTROLLERS

- General.  Provide Custom Application Controllers to provide the performance specified in section 1 of this division.  Each of these panels shall meet the following requirements.

- The Controller shall have sufficient memory to support its operating system, database, and programming requirements.

- Controllers that perform scheduling shall have a real time clock.

- The operating system of the Controller shall manage the input and output communications signals to allow distributed controllers to share real and virtual point information and allow central monitoring and alarms.

- The Controller shall continually check the status of its processor and memory circuits.  If an abnormal operation is detected, the controller shall assume a predetermined failure mode, and generate an alarm notification.

- Custom application controllers shall communicate using LonTalk, BACnet MSTP, or certified Zigbee.

- Environment.  Controller hardware shall be suitable for the anticipated ambient conditions.

- Controller used in conditioned ambient shall be mounted in IP 20 type enclosures, and shall be rated for operation at 0 C to 50 C [32 F to 120 F].

  - Memory.  The Controller shall maintain all BIOS and programming information in the event of a power loss for at least 72 hours.

  - Immunity to power and noise.  Controller shall be able to operate at 90% to 110% of nominal voltage rating and shall perform an orderly shutdown below 80% nominal voltage.

- APPLICATION SPECIFIC CONTROLLERS

- General. Application specific controllers (ASC) are microprocessor-based DDC controllers, which through hardware or firmware design are dedicated to control a specific piece of equipment.  They are not fully user programmable, but are customized for operation within the confines of the equipment they are designed to serve.

- Each ASC shall be capable of stand-alone operation and shall continue to provide control functions without being connected to the network.

- Each ASC will contain sufficient I/O capacity to control the target system.

- Environment.  The hardware shall be suitable for the anticipated ambient conditions.

- Controller used in conditioned ambient spaces shall be mounted in IP 20 type rated enclosures.  Controllers located where not to be disturbed by System activity (such as above ceiling grid), may be provided with plenum-rated enclosures and non-enclosed wiring connections for plenum cabling.  All controllers shall be rated for operation at 0 C to 50 C [32 F to 120 F].

- Controllers used outdoors and/or in wet ambient shall be mounted within IP 56 type waterproof enclosures, and shall be rated for operation at -40 C to 65 C [-40 F to 150 F].

  - Memory.  The Application Specific Controller shall maintain all BIOS and programming information in the event of a power loss for at least 90 days.

  - Immunity to Power and noise.  Controller shall be able to operate at 90% to 110% of nominal voltage rating and shall perform an orderly shutdown below 80%.

  - Transformer.  Power supply for the ASC must be rated at minimum of 125% of ASC power consumption, and shall be fused or current limiting type.

- INPUT/OUTPUT INTERFACE

- Hard-wired inputs and outputs may tie into the system through Building, Custom, or Application Specific Controllers.

- All input points and output points shall be protected such that shorting of the point to itself, another point, or ground will cause no damage to the controller.  All input and output points shall be protected from voltage up to 24V of any duration, such that contact with this voltage will cause no damage to the controller.

- Binary inputs shall allow the monitoring of on/off signals from remote devices.  The binary inputs shall provide a wetting current of at least 12 mA to be compatible with commonly available control devices.

- Pulse accumulation input points.  This type of point shall conform to all the requirements of Binary Input points, and also accept up to 3 pulses per second for pulse accumulation, and shall be protected against effects of contact bounce and noise.

- Analog inputs shall allow the monitoring of low voltage (0-10 Vdc), current (4-20 mA), or resistance signals (thermistor, RTD).  Analog inputs shall be compatible with, and field configurable to commonly available sensing devices.

- Binary outputs shall provide for on/off operation. Terminal unit and zone control applications may use 2 outputs for drive-open, drive-close (tri-state) modulating control.

- Analog outputs shall provide a modulating signal for the control of end devices.  Outputs shall provide either a 0-10 Vdc or a 4-20 mA signal as required to provide proper control of the output device.

- AUXILIARY CONTROL DEVICES

- Motorized dampers, unless otherwise specified elsewhere, shall be as follows:

  - Damper frames shall be 16 gauge galvanized sheet metal or 1/8" extruded aluminum with reinforced corner bracing.

  - Damper blades shall not exceed 8" in width or 48" in length. Blades are to be suitable for medium velocity performance (2,000 fpm).  Blades shall be not less than 16 gauge.

  - Damper shaft bearings shall be as recommended by manufacturer for application.

  - All blade edges and top and bottom of the frame shall be provided with compressible seals.  Side seals shall be compressible stainless steel.  The blade seals shall provide for a maximum leakage rate of 10 CFM per square foot at 2.5" w.c. differential pressure.

  - All leakage testing and pressure ratings will be based on AMCA Publication 500.

  - Individual damper sections shall not be larger than 48" x 60".  Provide a minimum of one damper actuator per section.

- Control dampers shall be parallel or opposed blade types as scheduled on drawings.

- Electric damper/valve actuators.

  - The actuator shall have electronic overload or digital rotation sensing circuitry to prevent damage to the actuator throughout the rotation of the actuator.

  - Where shown, for power-failure/safety applications, an internal mechanical, spring return mechanism shall be built into the actuator housing.

  - All rotary spring return actuators shall be capable of both clockwise and counter clockwise spring return operation.  Linear actuators shall spring return to the retracted position.

  - Proportional actuators shall accept a 0-10 VDC or 0-20 mA control signal and provide a 2-10 VDC or 4-20 mA operating range.

  - All non-spring return actuators shall have an external manual gear release to allow manual positioning of the damper when the actuator is not powered.  Spring return actuators with more than 60 in-lb. torque capacity shall have a manual crank for this purpose.

  - Actuators shall be provided with a conduit fitting and a minimum 1m electrical cable and shall be pre-wired to eliminate the necessity of opening the actuator housing to make electrical connections.

  - Actuators shall be Underwriters Laboratories Standard 873 listed.

  - Actuators shall be designed for a minimum of 60,000 full stroke cycles at the actuator's rated torque.

- Control Valves

  - Control valves shall be two-way or three-way type for two-position or modulating service as scheduled or shown.

  - Close-off (differential) Pressure Rating:  Valve actuator and trim shall be furnished to provide the following minimum close-off pressure ratings:

- Water Valves:

  - Two-way: 150% of total system (pump) head.

  - Three-way: 300% of pressure differential between ports A and B at design flow or 100% of total system (pump) head.

- Steam Valves: 150% of operating (inlet) pressure.

  - Water Valves:

- Body and trim style and materials shall be per manufacturer's recommendations for design conditions and service shown, with equal percentage ports for modulating service.

- Sizing Criteria:

  - Two-position service: Line size.

  - Two-way modulating service: Pressure drop shall be equal to twice the pressure drop through heat exchanger (load), 50% of the pressure difference between supply and return mains, or [5] psi, whichever is greater.

  - Three-way Modulating Service: Pressure drop equal to twice the pressure drop through the coil exchanger (load), [5] psi maximum.

  - Valves 1/2" through 2" shall be bronze body or cast brass ANSI Class 250, spring loaded, Teflon packing, quick opening for two-position service.  Two-way valves to have replaceable composition disc, or stainless steel ball.

  - 2-1/2" valves and larger shall be cast iron ANSI Class 125 with guided plug and Teflon packing.

- Water valves shall fail normally open or closed as scheduled on plans or as follows:

  - Heating coils in air handlers - normally open.

  - Chilled water control valves - normally closed.

  - Other applications - as scheduled or as required by sequence of operation.

- Zone valves shall be sized to meet the control application and they shall maintain their last position in the event of a power failure.

- Binary Temperature Devices- THERMOSTATS

  - Low-Voltage Space Thermostats shall be 24 V, bimetal-operated, mercury-switch type, with either adjustable or fixed anticipation heater, concealed setpoint adjustment, 13°C-30°C (55°F-85°F) setpoint range, 1°C (2°F) maximum differential, and vented cover. Provide with an digital Temperature readout and an override button for occupied areas.  Thermostats located in unoccupied areas do not require an override or digital readout.

  - Line-Voltage Space Thermostats shall be bimetal-actuated, open-contact type or bellows-actuated, enclosed, snap-switch type or equivalent solid-state type, with heat anticipator, UL listing for electrical rating, concealed setpoint adjustment, 13°C-30°C (55°F-85°F) setpoint range, 1°C (2°F) maximum differential, and vented cover.

  - Low-Limit airstream thermostats shall be UL listed, vapor pressure type. Element shall be at least 6 m (20 ft) long. Element shall sense temperature in each 30 cm (1 ft) section and shall respond to lowest sensed temperature. Low-limit thermostat shall be manual reset only.

- Temperature Sensors

  - Temperature sensors shall be Resistance Temperature Device (RTD) or Thermistor.

  - Duct sensors shall be rigid or averaging as shown. Averaging sensors shall be a minimum of 1.5m [5 feet] in length.

  - Immersion sensors shall be provided with a separable stainless steel well.  Pressure rating of well is to be consistent with the system pressure in which it is to be installed.

  - Space sensors shall be equipped with set-point adjustment, override switch, display, and/or communication port as shown on the drawings.

  - Provide matched temperature sensors for differential temperature measurement.  Differential accuracy shall be within 0.1 C [0.2 F].

  - Zone Sensors utilizing wireless technology shall conform to the following:

    - To check for proper operation, wireless zone temperature sensors shall include a signal strength and battery condition indicators on the zone sensor display or using LED’s on non-display models.

    - To allow local troubleshooting without specialized tools, error codes shall be displayed on the digital display through a blinking pattern on the non-display models. Error codes shall include: not associated, address to 000, improper software configuration, input voltage too high, or general sensor failure. Codes shall be indicated on inside of sensor back cover.

    - To support use by the physically impaired, the wireless zone sensor shall be a minimum font size of 12 points, and the LCD model shall be readable in low light conditions.

    - The wireless zone sensor shall include a readily visual indication of battery condition. The battery indication lights shall flash periodically for a minimum of 5 days to indicate the need for battery replacement prior to failure.

    - To ensure proper system performance, the wireless zone sensors shall automatically determine when the space temperature is rapidly changing. When the space temperature is readily changing, the space temperature shall be transmitted at least once each 30 seconds. The maximum time between transmissions shall be 15 minutes. Zone temperature sensing accuracy shall be +/- 0.5F (+/- 0.28C).

    - The wireless zone sensor battery life shall provide at least 5 years life under normal operating conditions and must be readily available size AA, 1.5V.

- Humidity Sensors

  - Duct and room sensors shall have a sensing range of 20% to 80% with accuracy of ±5% R.H.

  - Duct sensors shall be provided with a sampling chamber.

  - Outdoor air humidity sensors shall have a sensing range of 20% to 95% R.H.  It shall be suitable for ambient conditions of -40° C to 75° C [-40° F to 170° F].

  - Humidity sensor's drift shall not exceed 1% of full scale per year.

- Static Pressure Sensors

- Sensor shall have linear output signal.  Zero and span shall be field-adjustable.

- Sensor sensing elements shall withstand continuous operating conditions plus or minus 50% greater than calibrated span without damage.

- Water pressure sensor shall have stainless steel diaphragm construction, proof pressure of 150 psi minimum.  Sensor shall be complete with 4-20 mA output, required mounting brackets, and block and bleed valves.  Mount in location accessible for service.

- Water differential pressure sensor shall have stainless steel diaphragm construction, proof pressure of 150 psi minimum.  Over-range limit (DP) and maximum static pressure shall be 3,000 psi.  Transmitter shall be complete with 4-20 mA output, required mounting brackets, and five-valve manifold.  Mount in a location accessible for service.

  - Low Limit Thermostats

    - Safety low limit thermostats shall be vapor pressure type with an element 6m [20 ft] minimum length.  Element shall respond to the lowest temperature sensed by any one foot section.

    - Low limit shall be manual reset only.

  - Flow Switches

    - Flow-proving switches shall be either paddle or differential pressure type, as shown.

    - Paddle type switches (water service only) shall be UL listed, SPDT snap-acting with pilot duty rating (125 VA minimum).  Adjustable sensitivity with NEMA 1 Type enclosure unless otherwise specified.

    - Differential pressure type switches (air or water service) shall be UL listed, SPDT snap-acting, pilot duty rated (125 VA minimum), NEMA 1 Type enclosure, with scale range and differential suitable for intended application, or as specified.

    - Current sensing relays may be used for flow sensing or terminal devices.

  - Relays

    - Control relays shall be UL listed plug-in type with dust cover.  Contact rating, configuration, and coil voltage suitable for application.

    - Time delay relays shall be UL listed solid-state plug-in type with adjustable time delay.  Delay shall be adjustable plus or minus 200% (minimum) from set-point shown on plans. Contact rating, configuration, and coil voltage suitable for application.  Provide NEMA 1 Type enclosure when not installed in local control panel.

  - Transformers and Power Supplies

    - Control transformers shall be UL listed, Class 2 current-limiting type, or shall be furnished with over-current protection in both primary and secondary circuits for Class 2 service.

    - Unit output shall match the required output current and voltage requirements.  Current output shall allow for a 50% safety factor.  Output ripple shall be 3.0 mV maximum Peak-to-Peak.  Regulation shall be 0.10% line and load combined, with 50 microsecond response time for 50% load changes. Unit shall have built-in over-voltage protection.

    - Unit shall operate between 0° C and 50° C.

    - Unit shall be UL recognized.

  - Current Switches

    - Current-operated switches shall be self-powered, solid state with adjustable trip current.  The switches shall be selected to match the current of the application and output requirements of the DDC system.

  - Local Control Panels

    - All indoor control cabinets shall be fully enclosed NEMA 1 Type construction with hinged door, and removable sub-panels or electrical sub-assemblies.

    - Interconnections between internal and face-mounted devices shall be pre-wired with color-coded stranded conductors neatly installed in plastic troughs and/or tie-wrapped.  Terminals for field connections shall be UL listed for 600-volt service, individually identified per control/interlock drawings, with adequate clearance for field wiring.  Control terminations for field connection shall be individually identified per control drawings.

    - Provide on/off power switch with over-current protection for control power sources to each local panel.

  - ELECTRICAL METERS

- Contractor shall refer to electrical plans for locations of locations and quantity of meters.  A graphic shall be provided that shows all meter data.

- The power meter shall be fully electronic with multi-line backlit LCD display showing measured parameters.

- The power meter shall perform the following measurements:

- Accumulated Real Energy (kWh) for each phase and total of all phases

- Accumulated Reactive Energy (kVARh) and Apparent Energy (kVAh) totals for all phases

- Net Present Demand for Real (kW), Reactive (kVAR) and Apparent (kVA) Power over a user-specified interval (block or sliding window)

- Maximum (Peak) Real (kW), Reactive (kVAR) and Apparent (kVA) Demand Intervals

- Instantaneous Real (kW), Reactive (kVAR) and Apparent Power (kVA), by phase and in total

- Current (amps) for each phase and average of all phases

- Phase-to-phase voltage for each phase and average of all phase pairs

- Phase-to-neutral voltage for each phase pair and average of all phases

- Power factor for each phase and average of all phases

- AC frequency

- The power meter shall communicate using the BACnet MS/TP protocol at speeds from 9600 to 115,200 baud (no parity).  The meter shall provide a BACnet Device object, a set of writable Analog_Value objects for remote configuration, a set of Analog_Input objects to provide access to scaled 32-bit measurement values and their unit types, and a set of Binary_Input objects for indicating individual alarm conditions.

- The meter shall be UL/CUL listed to the latest applicable safety standards.

- Power meter models shall  accept voltage input over the range of 90 to 600 VAC (50 or 60 Hz).

- The power meter shall accept 0 to 0.333VAC input from up to three current transducers (U018 Rope Style CTs only) from 20 to 5000 amps.

- The measured energy consumption shall be retained in non-volatile memory for the life of the product warranty.

- The power meter shall have demand measurement programmable for up to 6 sub-intervals of 10 seconds to 546 minutes duration.

- Meter shall be optionally available in an outdoor NEMA 4X enclosure.

- The power meter shall operate from -30°C to +70°C.

- The power meter shall have dimensions not exceeding 4.2” x 3.6” x 2.3”.

- The power meter shall be Veris E50H5A or equivalent.

- The power meter shall meet both ANSI C12.20 0.5% and IEC 62053-22 Class 0.5S real power and energy accuracy specifications.

- The power meter shall meet IEC 62053-22 Class 2 reactive power and energy accuracy specifications.

- The power meter shall be configurable for operation on Single Phase (AN or AB), Split Phase (ABN), Delta (ABC), and Wye (ABCN) systems.

- The power meter shall have automatic phase reversal compensation such that it is insensitive to the CT’s load orientation.

- The power meter shall have separate control power inputs such that is may be powered from a different service than it measures.

- The power meter shall have two user-configurable Pulse Contact inputs to support measurement of other related energy values (gas, water, steam, etc.) over BACnet using simple pulse-output transducers.

- The power meter shall be configurable for use with potential transformers to 5000 volts.

- The power meter shall calculate a maximum theoretical system power using the configuration parameters set by the user.

- The power meter shall support warnings for low power factor (phase current or voltage miss-wired), current over range, voltage over range, and frequency out of range.

- The product shall have a 5-year warranty.

  - Lighting Control System

1.01 Description Of Work

Extent of lighting control system work is indicated by drawings and by the requirements of this section. It is defined to include, but not by way of limitation:

1.	Lighting Relay panel.  BMS installer shall provide the panel to the Division 26 Contractor to install.  Refer to Electrical Details for coordination requirements.  Wiring, switches, conduits by Division 26 Contractor unless noted otherwise.

2.	Master ON/OFF control capability

Types of lighting control equipment and wiring specified in this section include the following:

Low Voltage Remote Control Relay Panels

Master ON/OFF control capability

Requirements are indicated elsewhere in these specification for work including, but not limited to, raceways and electrical boxes and fitting required for installation on control equipment and wiring.

1.02 QUALITY ASSURANCE

Manufacturers: Firms regularly engaged in manufacture of lighting control equipment and ancillary equipment, of types and capacities required, whose products have been in satisfactory use in similar service for not less than 5 years.

Component Pretesting: All components and assemblies are to be factory pretested prior to installation.  Contractor shall verify requirements and if lights are to remain on, it is the Contractors responsibility to mark each switch during the burn in period.

NEC Compliance: Comply to NEC as applicable to electrical wiring work.

NEMA Compliance: Comply with applicable portions of NEMA standards pertaining to types of electrical equipment and enclosures.

UL Approvals: Remote panels are to be UL listed under UL 916 Energy Management Equipment.

FCC Emissions: All assemblies are to be in compliance with FCC emissions Standards specified in Part 15 Subpart J for Class A application.

1.04 SUBMITTALS

Product Data: Submit manufacturer's data on lighting control system and components.

Shop Drawings: Submit dimension drawings of all lighting control system components and accessories.

One Line Diagram: Submit a one line diagram of the system configuration proposed if it differs from that illustrated in the riser diagram included in these specifications.

Typical Wiring Diagrams: Submit typical wiring diagrams for all components including, but not limited to, relay panels, relays, low voltage switches, occupancy sensors, master ON/OFF sequencers, and daylighting controls.

2.01 - Basic Lighting Control System

A.	System Description

1.	The lighting control system shall consist of relay panel assemblies.  Refer to Electrical Details for division of responsibilities.  One panel shall be provided for each floor where circuits are to be controlled.  Three panels in total.  Relay panels shall be provided with a minimum of one additional spare relay per panel.

2.	The relay panels shall be mounted as indicated on the drawings. The numbered relays in the panel shall be wired to control the power to each load as indicated on the Panel Wiring Schedules included in the drawings. All power wiring will be identified with the circuit number controlling it at the load.

3.	All wiring shall comply with the wiring specifications.

- The panels shall provide a mounting bracket for the addition of master ON/OFF sequencers.  These devices shall be totally compatible with the manual operation of the low voltage switches and occupancy sensors; and, in the event of a sequencer or photocontrol failure, the switches and occupancy sensors shall continue to operate to provide relay control.

- The Division 26 Contractor shall provide the momentary switches, faceplates, junction boxes, and a conduit stubbed up above the ceiling.  The Division 25 contractor shall install the switches and faceplates provided by Division 26 and provide the wiring from the switch back to the relay cabinet.  Once above the ceiling, the Division 25 Contractor is responsible for providing the wireway.

B. Hardware Features

1.	Modular Relay Panels shall be UL listed and consist of the following:

a.	Tub: Empty NEMA 1 enclosure sized to accept the required number of relays to operate the number of circuits indicated on the Electrical Lighting Plans.  GE RR9P or RR7P relays or equal.

b.	Interior: Bracket and circuit board backplane. Interiors shall be sized to accept either 1-12, 1-24, or 1-48 relays.  Each relay be capable of direct ON/OFF control by a low voltage switch or occupancy sensor. Relays shall be momentary-pulsed mechanically latching contactors rated at 20 amps, 120-277 VAC. They shall attach to the Interior by a single plug-in connector.

c.	Power Supply: Transformer assembly with two 40VA transformers with separate secondaries; one providing power to relays and associated low voltage switches and sensors, the second providing power for accessory devices. Transformers include internal overcurrent protection with automatic reset and metal oxide varistor protection against powerline spikes.  120 VAC, 50/60 Hz. +/- 10%.

d.	Cover: Surface with captive screws in a hinged, lockable configuration.  A wiring schedule directory card shall be affixed to the cover's back to allow identification of circuits/relays/loads controlled when the door is open.

2. 	Master ON/OFF Sequencers

a. 	General

Panel Master ON/OFF capability will be provided by adding a Master ON/OFF sequencer to the panel.  The sequencer outputs will be wired to the ON(Red)/OFF(Black) terminals of the relays to be included in the Master Group.  The Master Sequencer shall provide ON/OFF control of the group while still allowing individual relays to be overridden by their local switches.

b. Hardware Features

1.	Each sequencer shall allow for either all ON or all OFF operation, thus doubling the number of relays it may control.

3. 	Each sequencer shall have two independent switch input channels.  These switch inputs may be either 2 or 3-wire, maintained or momentary dry contact.

1.	All of the relays in a panel shall be sequenced ON/OFF in less than 4 seconds.

2.	Each output shall be capable of operating up to 3 relays in parallel.

- SEQUENCE OF OPERATIONS

General- All inputs (temperatures, pressures, times, etc) shall be adjustable.

- DEDICATED OUTSIDE AIR UNITS SYSTEM

OCCUPANCY

- Unit shall enter occupied or unoccupied mode based on schedule as communicated by the BMS.

  - Occupied: The controller shall perform the following operations in occupied mode:

- Outside air damper shall be energized to fully open.

- Supply and exhaust fans shall enable.

- Energy wheel shall enable.

- Hot/chilled water pump shall be enabled

- The face and bypass dampers shall modulate to maintain DAT setpoint. The user shall be given the ability to define separate heating mode and cooling mode DAT setpoints which will both be 72°F by default

  - Unoccupied: The controller shall perform the following operations in unoccupied mode:

- Hot/chilled water coil pump shall be disabled.

- After 30 seconds (adj.) the supply fan, exhaust fan, and energy wheel shall be disabled.

- Outside air damper shall be de-energized and fail closed.

- Return air damper shall be de-energized and fail open.

HEATING/COOLING MODE

- Mode determination shall only take place when the unit is the occupied mode

- When the temperature entering the coil ≤ 66°F heating shall be enabled and the following shall occur:

    - Flow shall be proven for 30 seconds at the hot/chilled water pump

    - The WWHP shall enabled and commanded to heating mode

    - The WWHP compressors shall stage to maintain a user adjustable heating setpoint tank temperature of 120°F

- When the temperature entering the coil ≥ 74°F cooling shall be enabled and the following shall occur:

    - Flow shall be proven for 30 seconds at the hot/chilled water pump

    - The WWHP shall enabled and commanded to cooling mode

    - The WWHP compressors shall stage to maintain a user adjustable cooling setpoint tank temperature of 45°F

- The two position 3-way valve at the AHU shall be normally open, spring return, such that a failure allows flow through the AHU coil. Anytime the hot/chilled water storage tank is more than 10°F from setpoint the valve shall be powered closed such that flow bypasses the AHU until the tank setpoint is met.

ENERGY RECOVERY

- Upon entering the occupied mode of operation, the controller shall enable the energy recovery sequence if one of the following conditions is met:

- The outdoor air temperature is 5°F (adj.) below the return air temperature

- The outdoor air temperature is 5°F (adj.) above the return air temperature

- The return air relative humidity is above 63% RH (adj.).

- Unit is in heating mode.

If the exhaust air temperature drops below 35°F (adj.), the controller shall perform the following operations:

- Energy wheel de-energized for 90 seconds.

- Energy wheel energized for 3 minutes.

DEHUMIDIFICATION

- Dehumidification mode shall be enabled if the return air relative humidity is 63% or higher.

- In dehumidification mode the following sequence shall occur:

  - The WWHP shall be forced into cooling mode

  - The AHU coil face and bypass dampers shall be positioned such that 25% of the total airflow passes through the coil

- The unit shall release from dehumidification mode and return to its previous state once the return relative humidity drops below 55%

FREEZE PROTECTION

- Anytime the entering air temperature to the coil is 35°F or below the pump serving the unit shall be enabled.

MECHANICAL ROOM

- OCCUPIED AND UNOCCUPIED OPERATION

The building variable speed loop pumping system shall start to provide water flow to the heat pumps if any heat pump starts during the unoccupied time.  The variable speed pumping system shall remain on for 30 minutes (adjustable) to prevent short cycling of the equipment.

OCCUPIED AND TRANSITION FROM UNOCCUPIED TO OCCUPIED OPERATION

The building variable speed loop pumping system shall start to provide water flow to the heat pumps during the transition sequences from unoccupied to occupied and remain on during the occupied schedule.

- VARIABLE SPEED LOOP PUMP CONTROL

Each of the two loop pumps shall have a dedicated variable frequency drive with 3-contactor bypass.  Pump lead / lag shall be provided to equalize run hours on each pump.  The order of the pump lead / lag sequence shall be rotated every 7 days (adjustable). The lag pump shall automatically start upon failure of the lead pump. The FMS shall monitor one loop differential pressure sensor(s) as indicated on the plans and modulate the lead pump variable frequency drive to maintain the critical run pipe pressure set point (adjustable).  Refer to the loop piping layout for the sensor location(s).  Refer to the points list for complete monitoring and control points.

The variable frequency drives are to be provided and installed by others. The BAS contractor is responsible for hardwiring start/stop, status, and speed signals as well as integrating via BACnet/mstp and pulling all available data into the BAS.

- RADIANT HEAT SYSTEM

Each floor will have its own two position, three way control valve as shown on the plans to control the radiant heat by floor. The valves shall be normally closed spring return such that upon failure water bypasses the heaters. Normally the valves will open anytime the radiant heat system pump is enabled. The user shall have the ability to override the operation of each control valve to enable/disable heat by floor.

The radiant heat system pumps shall be enabled anytime the outside air temperature falls below 50°F (adj) during the occupied mode or below 35°F in unoccupied mode. The system shall be on its own schedule to determine occupancy and shall utilize optimal start. Pump lead / lag shall be provided to equalize run hours on each of the two redundant constant speed pumps that serve the radiant heat system.  The order of the pump lead / lag sequence shall be rotated every 7 days (adjustable). The lag pump shall automatically start upon failure of the lead pump.

The radiant heat system hot water tank shall maintain a temperature in the tank utilizing a linear reset according to the schedule below. A geothermal WWHP shall be enabled to maintain the HW Tank setpoint. Anytime the tank is more than 10°F below current setpoint the 3-way valves on each floor shall be closed, bypassing the heaters.

| OAT | HW Tank Setpoint |
| --- | --- |
| ≤ 50°F | 100°F |
| ≤ 35°F | 120°F |

- WATER SOURCE HEAT PUMPS

- Complete control of the water source heat pump unit variable speed compressor and supply air fan are to be provided by a factory mounted BACnet/mstp or LON controller. The Building Automation System (BAS) shall send the ASC the occupied space heating and cooling temperature setpoints. The BAS shall also send the following commands: 

Occupied                                 
Unoccupied                               
Heat/Cool Mode                           
Priority Shutdown Commands               
If communication with the BAS is lost, the ASC shall use predetermined default setpoints and operate in the occupied mode.

- OCCUPIED

- During occupied periods the supply fan will run continuously and the outside air damper will open.  The DX cooling will be enabled to maintain the active space temperature setpoint.

- SPACE TEMPERATURE CONTROL

- The space temperature shall be maintained between the occupied cooling setpoint (72°F adj) and the occupied heating setpoint (70°F adj).  The unit will transition to the cooling mode when the space temperature rises one degree above the occupied cooling setpoint (72°F adj).  The unit will transition to the heating mode when the space temperature drops one degree below the occupied heating setpoint (70°F adj).

- UNOCCUPIED (NIGHT SETBACK)

- When the space temperature is above the unoccupied cooling setpoint (85°F adj) the supply fan will start, the outside air damper will remain closed and the DX cooling will be enabled.  When the space temperature falls below the unoccupied cooling setpoint (85°F adj) minus the unoccupied differential (2°F adj) the supply fan will stop and the DX cooling will be disabled.

- MORNING COOL DOWN

- During optimal start, if the space temperature is 3°F above the occupied cooling setpoint, a morning cool-down sequence will be activated.  The supply fan will start, the outside air damper will remain off, and the cooling will be enabled to lower the space temperature to the occupied cooling setpoint.  The outside air damper will remain closed.  Mode will terminate when the space temperature reaches the occupied cooling setpoint.

- SUPPLY FAN OPERATION

- The fan will be off in the unoccupied mode.  If the supply fan fails the fan will be commanded off and an alarm will be annunciated.  A manual reset is required to restart the fan.

- WATER ISOLATION VALVE

- The factory mounted controller shall support a two-position water isolation valve without needing any special configuration

  - IsolationValve “ON” Control - The isolation valve output will be energized (controlled open) during compressor heating, compressor cooling, dehumidification, and when forced open during manual output override testing. When the isolation valve is driven open for compressor operation, the output will be energized 20 seconds prior to the compressor and indoor fan (if not already energized) outputs to ensure adequatewater flow to the heat exchanger.To reduce excessive cycling of the isolation valve, once opened, the isolation valve will remain open for a minimum of 10 minutes.

  - IsolationValve “OFF” Control - The isolation valve output will be de-energized (controlled closed) when there is no longer a call for compressor operation and the 10 min. minimum on time has expired or the manual output override test has driven it closed.

- REVERSING VALVE

- For normal unit operation, the reversing valve output is energized when the unit is in Cooling mode and de-energized in Heating mode. If de-energized, the reversing valve output shall be energized for Cooling when the compressor output is energized and the compressor speed has ramped up to the proper startup speed. Once energized, the reversing valve output will remain energized until the controller energizes the compressor output for heating and the compressor speed has ramped up to the startup speed for heating or the Unit Mode is set to Off. When a power-failure occurs, the reversing valve output defaults to the heating (de-energized) state.

- LIGHTING CONTROLS

  - The lighting controls shall serve public areas, corridors, and open work stations.  Each zone shall include a separate schedule.  Lighting shall be off at the programmed time.  Five minutes prior to the lights being shut off, the lights shall blink.  If the occupant turns on the light, it shall override that area for one hour.  In the morning, all corridor lighting shall be on at scheduled time.  Open work station areas shall be turned on by the local switch.

- DOMESTIC HOT WATER

- The hot water tank shall operate independently to maintain temperature.  The recirculation pump shall be controlled to maintain the return hot water temperature to 110 deg F during occupied hours.  Provide temperature sensor in supply and recirculation line.

- RADIANT ELECTRIC CEILING HEATER (CH-X)

  - During occupied periods the ceiling heater will run to maintain occupied setpoint temperature (adjustable) as detected by wall-mounted temperature sensor (see plans). During unoccupied periods, the ceiling heater will run to maintain unoccupied setpoint temperature (adjustable) as detected by wall-mounted temperature sensor (see plans).

REFER TO POINTS LIST.

END OF CONTROLS – DIRECT DIGITAL