SECTION 202500 - HANGERS, CLAMPS, ATTACHMENTS, ETC.

- GENERAL

  - The Contractor's attention is directed to the General and Special Conditions, General Provisions - Mechanical and to all other Contract Documents as they apply to this branch of the work.  Attention is also directed to other sections of the Contract Documents which affect the work of this section and which are hereby made a part of the work specified in this section.

  - Each Contractor's attention is also directed to Section 201300, Pipe, Pipe Fittings and Pipe Support.

  - This section includes, but is not limited to, furnishing and installing dampers, supports, anchors, and accessories for piping, ductwork, equipment, etc.  Furnishing and installing shall be by each trade for the completion of their work.

  - Power driven anchors and expansion anchors shall be permitted only when permission is granted in writing by the Architect and Engineer.

- MATERIALS AND EQUIPMENT

  - Hangers, Clamps, Attachments, Etc.:

|  | SIZE | SPECIFICATION |
| --- | --- | --- |
| 1. Pipe Rings | 2" pipe and smaller | Adjustable swivel split ring or split pipe ring, Grinnell Figures 104 and 108, Elcen, Fee & Mason, or approved equivalent. |
| 2. Pipe Clevis | 2-1/2" pipe and larger | Adjustable wrought Clevis type, Grinnell Figure 260, Elcen, Fee & Mason, or approved equivalent. |
| 3. Pipe Clevis | All | Steel Clevis for insulated pipe, Elcen Figure 12A, Grinnell, Fee & Mason or approved equivalent. |
| 4. Rise Clamps | All | Extension pipe or riser clamp, Grinnell Figure 261, Elcen, Fee & Mason or approved equivalent. |
| 5. Beam Clamps and Attachments | All | Grinnell Figure numbers listed or, Elcen, Fee & Mason, or approved equivalent. Malleable beam clamp with extension piece figure 229; I-beam clamp figure 131; C-clamp figures 83, 84, 85, 86, 87, and 88. |
| 6. Brackets | All | Welded steel brackets medium weight, Grinnell Figure 195, Elcen, Fee & Mason or approved equivalent. |
| 7. Concrete Inserts | All | Grinnell Figure numbers listed or, Elcen, Fee & Mason or approved equivalent. Wrought steel insert Figure 280 and wedge type insert Figure 281. |
| 8. Concrete Fasteners | All | Self-drilling concrete inserts, Phillips, Grinnell, Elcen or approved equivalent. |
| 9. Ceiling | All | Grinnel Figure numbers listed or Elcen, Fee & Mason, or approved equivalent. Pipe hanger flange Figure 153, adjustable swinging hanger flange Figure 155, ceiling flanges Figures 128 and 128R, and adjustable ceiling flange Figure 116. |
| 10. Rod Attachments | All | Grinnel Figure numbers listed or Elcen, Fee & Mason, or approved equivalent. Extension piece Figure 157, rod coupling Figure 136, and forged steel turnbuckle Figure 230. |
| 11. U-Bolts | All | Standard, U-bolt, Grinnell Figure 137, Elcen, Fee & Mason, or approved equivalent. |
| 12. Welded Pipe Saddles | All | Pipe covering protection saddle sized for thickness of insulation, Grinnell Figure 186, Elcen, Fee & Mason or approved equivalent. |
| 13. Pipe Roll | All | Adjustable swivel pipe roll, Grinnell Figure 174, Elcen, Fee & Mason, or approved equivalent. |
| 14. Protection Saddle | All | 18 gauge sheet metal pipe protection saddle, Elcen Figure 219, Fee & Mason, Power Strut, or approved equivalent. |
| 15. Hanger Rods | All | Steel, diameter of the hanger threading, ASTM A-107. |
| 16. Miscellaneous Steel | All | Steel angles, rods, bars, channels, etc., used in framing for supports and fabricated brackets, anchors, etc., shall conform to ASTM-A-7. |
| 17. Concrete Channel Inserts | All | Continuous slot inserts, Unistrut, or approved equivalent. Heavy duty Series P-3200 or Light Duty Series P-3300 as required. |
| 18. Adjustable Spot Insert | All | Adjustable spot insert Unistrut, or approved equivalent, P-3245. Design load 1000 lbs. |

- INSTALLATION

  - Unless otherwise specifically indicated or hereinafter specified in the specifications, all supporting, hanging and anchoring of piping, ductwork, equipment, etc., shall be done by each trade as is necessary for completion of the work and shall be as directed in the following paragraphs:

    - The building structure and fireproofing may be in place prior to Bid Package #3 being awarded.  Supports and anchors shall be coordinated with the fireproofing to minimize impact.

    - Supporting and hanging shall be done so that excessive load will not be placed on any one hangers so as to allow for proper pitch and expansion of piping.  Hangers and supports shall be placed as near as possible to joints, turns and branches.

    - For concrete construction, utilize adjustable concrete inserts for fasteners.  Expansion anchors and power driven devices may be used when approved in writing by the Architect/Engineer.  Utilize beam clamps for fastening to steel joists and beams and expansion anchors in masonry construction.  When piping is run in joists, piping shall be top mounted on trapeze type hangers with each pipe individually clamped to trapeze hanger.

    - Trapeze hangers shall be supported by steel rods of sufficient diameter to support piping from joists or concrete construction.  Where desired or required, piping may be double mounted on trapeze hangers.  Where conditions permit, trapeze hangers may be surface mounted on exposed joists by means of approved beam clamps, or to concrete construction by means of approved adjustable inserts or expansion anchors.

    - Install all miscellaneous steel other than designed building structural members as required to provide means of securing hangers, supports, etc., where piping does not pass directly below or cross steel joists.

    - Piping shall not be supported by the equipment to which it is connected.  Support all piping so as to remove any load or stress from the equipment.

    - Where piping, etc., is run vertically, approved riser clamps, brackets or other means shall be utilized at approximately 10'-0" center to center minimum and an approved adjustable base stand or fitting on concrete support base shall be utilized at the base of the vertical run.

    - Where piping is run along walls, knee braced angle frames or pipe brackets with saddles, clamps, and rollers (where required) mounted on structural brackets fastened to walls or columns shall be used.

    - Support all ceiling hung equipment, with approved vibration isolators.

    - Where copper tubing is specified, hangers shall be of copper clad type when piping is uninsulated.

    - Uninsulated piping hung from above shall be supported with ring and clevis type pipe hangers.  Uninsulated piping mounted on trapeze and wall bracket type support shall be held in place with U-bolts.  U-bolts shall allow for axial movement in the piping.

    - All insulated piping shall be supported with clevis type and/or pipe roll hangers.  Hangers shall be sized to allow the pipe insulation to pass through the hangers.  Install insulation protection saddles at all hanger locations.  Welded pipe saddles shall be installed at all hangers on piping 5" and larger.  The pipe saddles shall be sized for the thickness of insulation used.  Hangers shall fit snugly around outside of insulation saddles.

    - Under no conditions will perforated band iron or steel wire driven hangers be permitted.

    - In general, support piping at the following spacing:

      - Steel and copper piping - 8 foot intervals for piping 3" and smaller; 10 foot intervals for larger piping.

      - Polyethylene piping – 4 foot intervals for piping 2” and smaller.  5 foot intervals for 3” pipe.  6 foot intervals for 4”, 6”, and 8” pipe.

      - PVC piping – 4 foot intervals for piping 1 1/2” and smaller.  5 foot intervals for 2 and 2 ½” piping.  6 foot intervals for 3” pipe and larger.

      - Where the manufacturer of the pipe has more strict guidelines, the manufacturer’s recommendations shall be followed.

END OF HANGERS AND CLAMPS