## 100% OAU
SYSTEM POINT
DESCRIPTION |  | ANALOG | [13 empty] | BINARY | [10 empty] | SYSTEM FEATURES
|  | INPUT | [9 empty] | OUTPUT |  |  |  | INPUT |  |  |  |  | OUTPUT | [5 empty] | ALARMS | [9 empty] | PROGRAMS
OUTSIDE AIR SYSTEM | GRAPHIC | TEMPERATURE | PRESSURE | RH | KW | GPM | CFM | PPM | PERCENT | USER OVERIDE AVAIL | SOFTWARE SETPOINT | DDC | CAPACITY | SETPOINT ADJ. | SPEED | PNEU. TRANSDUCER | STATUS ON / OFF | FILTER STATUS | STATUS OPEN / CLSD. | STATUS | OFF / ON | OPEN / CLOSED | LOCKOUT | ENABLE / DISABLE | HIGH / LOW | AUTO/STOP | HIGH ANALOG | LOW ANALOG | BINARY | PROOF | SENSOR FAIL | FLOW FAIL | COMM. FAIL | DIAGNOSTICS | LATCHING | LIMIT WARNING | TIME SCHEDULING | OPT. START / STOP | DEMAND LIMITING | RESET | EVENT PROGRAM | DDC | ALARM INSTRUCT | MAINT. WK. ORDER | RUN TIME | EXP. MESSAGE | SET BACK / SET UP | NIGHT PURGE | TENANT BILLING | CHILLER SEQUENCING | TOTALIZING | TIMED OVERRIDE | MODE CONTROL | NOTES:
SUPPLY FAN | X | [15 empty] | X |  |  |  | X | [15 empty] | X | [16 empty] | 1
COIL ENTERING AIR TEMP | X | X | [24 empty] | X | X |  |  | X | [21 empty] | X
EXHAUST FAN | X | [15 empty] | X |  |  |  | X | [15 empty] | X | [16 empty] | 1
EXHAUST AIR TEMP | X | X
ENERGY WHEEL | X | [19 empty] | X
AHU BYPASS VALVE | X | [20 empty] | X
FACE AND BYPASS DAMPERS | X | [7 empty] | X | X
DISCHARGE AIR TEMPERATURE | X | X | [7 empty] | X | [16 empty] | X | X
OUTSIDE AIR DAMPER | X | [20 empty] | X | [14 empty] | X
RETURN AIR DAMPER | X | [20 empty] | X | [14 empty] | X
RETURN AIR TEMP | X | X | [24 empty] | X | X
RETURN AIR HUMIDITY | X |  |  | X | [22 empty] | X
FILTER |  |  | X | [25 empty] | X |  |  |  |  | X | [9 empty] | X
FREEZE STAT | [19 empty] | X | [8 empty] | X | [5 empty] | X
OCCUPANCY | [9 empty] | X | [26 empty] | X
DEHUMIDIFICATION SETPOINT | [9 empty] | X | X
DISCHARGE AIR TEMPERATURE COOLING SETPOINT | [9 empty] | X | X
DISCHARGE AIR TEMPERATURE HEATINGING SETPOINT | [9 empty] | X | X
ENTERING WWHP TEMP | X | X | [24 empty] | X | X
LEAVING WWHP TEMP | X | X | [24 empty] | X | X
HEAT/COOL MODE | X | [20 empty] | X | [30 empty] | X
COMPRESSOR 1 | X | [19 empty] | X | [15 empty] | X
COMPRESSOR 2 | X | [19 empty] | X | [15 empty] | X
TANK TEMP | X | X | [24 empty] | X | X | [25 empty] | 2
HOT/CHILLED WATER PUMP | X | [15 empty] | X |  |  |  | X
TANK COOLING MODE SETPOINT | [9 empty] | X | X
TANK HEATING MODE SETPOINT | [9 empty] | X | X
NOTES:
1) Equipment graphic shall be 3-D and animated to indicate status
2) Use insertion type temperature sensor. Strap-on not acceptable.

## WSHP
SYSTEM POINT
DESCRIPTION |  | ANALOG | [13 empty] | BINARY | [10 empty] | SYSTEM FEATURES
|  | INPUT | [9 empty] | OUTPUT |  |  |  | INPUT |  |  |  |  | OUTPUT | [5 empty] | ALARMS | [9 empty] | PROGRAMS
WSHP | GRAPHIC | TEMPERATURE | PRESSURE | RH | KW | GPM | CFM | PPM | PERCENT | PERCENT RLA | TONS | DDC | CAPACITY | SETPOINT ADJ. | SPEED | PNEU. TRANSDUCER | STATUS ON / OFF | FILTER STATUS | STATUS OPEN / CLSD. | STATUS | OFF / ON | OPEN / CLOSED | LOCKOUT | ENABLE / DISABLE | HIGH / LOW | AUTO/STOP | HIGH ANALOG | LOW ANALOG | BINARY | PROOF | SENSOR FAIL | FLOW FAIL | COMM. FAIL | DIAGNOSTICS | LATCHING | LIMIT WARNING | TIME SCHEDULING | OPT. START / STOP | DEMAND LIMITING | RESET | EVENT PROGRAM | DDC | ALARM INSTRUCT | MAINT. WK. ORDER | RUN TIME | EXP. MESSAGE | SET BACK / SET UP | NIGHT PURGE | TENANT BILLING | CHILLER SEQUENCING | TOTALIZING | TIMED OVERRIDE | MODE CONTROL | NOTES:
ZONE SENSOR | X | X | [11 empty] | X | [12 empty] | X | X |  |  | X | [5 empty] | X | X | [8 empty] | X |  |  |  |  | X |  | 1
DISCHARGE AIR TEMP | X | [25 empty] | X | X |  |  | X
REVERSING VALVE | [21 empty] | X | [30 empty] | X
FAN | X | [13 empty] | X |  | X |  |  |  | X | [32 empty] | 2, 3
ISOLATION VALVE | [21 empty] | X | [12 empty] | X
COMPRESSOR 1 | X | [13 empty] | X |  | X |  |  |  | X | [17 empty] | X | [14 empty] | 3
COMPRESSOR 2 | X | [13 empty] | X |  | X |  |  |  | X | [17 empty] | X | [14 empty] | 3
LEAVING WATER TEMPERATURE | X
CONDENSATE OVERFLOW | X | [18 empty] | X | [8 empty] | X | [5 empty] | X | [7 empty] | X | X
GENERAL ALARM | X | [16 empty] | X | [10 empty] | X |  | X | X | X | X | [8 empty] | X | X | [9 empty] | 4,5
NOTES:
1) Provide digital display, setpoint adjustment, and override on each zone sensor
2) Equipment graphic shall be 3-D and animated to indicate status
3) Speed is only required on variable speed units. Multiple compressors only where specified. See plans
4) Filter timer or differential pressure transmitter
5) Provide manufacturer alarm code key on WSHP graphic

## MECH RM
SYSTEM POINT
DESCRIPTION |  | ANALOG | [13 empty] | BINARY | [10 empty] | SYSTEM FEATURES
|  | INPUT | [9 empty] | OUTPUT |  |  |  | INPUT |  |  |  |  | OUTPUT | [5 empty] | ALARMS | [9 empty] | PROGRAMS
MECH RM | GRAPHIC | TEMPERATURE | PRESSURE | RH | KW | GPM | CFM | PPM | PERCENT | PERCENT RLA | BACNET INTEGRATION | DDC | CAPACITY | SETPOINT ADJ. | SPEED | PNEU. TRANSDUCER | STATUS ON / OFF | FILTER STATUS | STATUS OPEN / CLSD. | STATUS | OFF / ON | OPEN / CLOSED | LOCKOUT | ENABLE / DISABLE | HIGH / LOW | AUTO/STOP | HIGH ANALOG | LOW ANALOG | BINARY | PROOF | SENSOR FAIL | FLOW FAIL | COMM. FAIL | DIAGNOSTICS | LATCHING | LIMIT WARNING | TIME SCHEDULING | OPT. START / STOP | DEMAND LIMITING | RESET | EVENT PROGRAM | DDC | ALARM INSTRUCT | MAINT. WK. ORDER | RUN TIME | EXP. MESSAGE | SET BACK / SET UP | NIGHT PURGE | TENANT BILLING | CHILLER SEQUENCING | TOTALIZING | TIMED OVERRIDE | MODE CONTROL | NOTES:
PUMP 1 VFD | X | [9 empty] | X |  |  |  | X |  | X |  |  |  | X | [7 empty] | X | X |  | X |  | X |  |  | X | [16 empty] | 1
PU MP 2 VFD | X | [9 empty] | X |  |  |  | X |  | X |  |  |  | X | [7 empty] | X | X |  | X |  | X |  |  | X | [16 empty] | 1
ENTERING WELLFIELD TEMP | X | X | [24 empty] | X | X
LEAVING WELLFIELD TEMP | X | X | [24 empty] | X | X
LOOP DIFFERENTIAL PRESSURE | X |  | X | [23 empty] | X | X |  |  | X
MIN FLOW BYPASS | X | [20 empty] | X
OUTSIDE AIR | X | X |  | X
EJECTOR PUMP | X | [27 empty] | X | [24 empty] | 2
GENERAL NOTES:
1) Integrate to VFD by BACnet/mstp interface provided by manufacturer. Provide all available software points and alarms.
2) Monitor dry alarm contract provided by pump manufacturer.

## MISC
SYSTEM POINT
DESCRIPTION |  | ANALOG | [11 empty] | BINARY | [10 empty] | SYSTEM FEATURES
|  | INPUT | [9 empty] | OUTPUT |  | INPUT |  |  |  |  | OUTPUT | [5 empty] | ALARMS | [9 empty] | PROGRAMS
MISC | GRAPHIC | TEMPERATURE | PRESSURE | RH | KW | GPM | CFM | PPM | PERCENT | USER OVERIDE AVAIL | SOFTWARE SETPOINT | DDC | SETPOINT ADJ. | PNEU. TRANSDUCER | STATUS ON / OFF | FILTER STATUS | STATUS OPEN / CLSD. | STATUS | OFF / ON | OPEN / CLOSED | LOCKOUT | ENABLE / DISABLE | HIGH / LOW | AUTO/STOP | HIGH ANALOG | LOW ANALOG | BINARY | PROOF | SENSOR FAIL | FLOW FAIL | COMM. FAIL | DIAGNOSTICS | LATCHING | LIMIT WARNING | TIME SCHEDULING | OPT. START / STOP | DEMAND LIMITING | RESET | EVENT PROGRAM | DDC | ALARM INSTRUCT | MAINT. WK. ORDER | RUN TIME | EXP. MESSAGE | SET BACK / SET UP | NIGHT PURGE | TENANT BILLING | CHILLER SEQUENCING | TOTALIZING | TIMED OVERRIDE | MODE CONTROL | NOTES:
RADIANT HEAT VALVES | X | [8 empty] | X | [8 empty] | X | [15 empty] | X | X
RADIANT HEAT SYSTEM TANK TEMP | X | X | [49 empty] | 3
RADIANT HEAT SYSTEM PUMP | X | [13 empty] | X |  |  |  | X | [8 empty] | X |  | X | [21 empty] | 1
RADIANT HEAT SYSTEM TANK SETPOINT | X | [8 empty] | X | X | [23 empty] | X | X |  | X
PENTHOUSE SPACE TEMP | X | X | [22 empty] | X | X
ELEVATOR ROOM TEMP | X | X | [22 empty] | X | X
ELEVATOR ROOM EXHUAST FAN | X | [13 empty] | X |  |  |  | X | [8 empty] | X
ELEVATOR ROOM VENTILATE SETPOINT | X | [8 empty] | X | X | [40 empty] | 2
ELECTRIC METER |  |  |  |  | X | [43 empty] | X
X
GENERAL NOTES:
1) Equipment graphic shall be 3-D and animated to indicate status
2) Default setpoint is 85°F
3) Use insertion type temperature sensor. Strap-on not acceptable.