SECTION 202200 - INSULATION - MECHANICAL

- GENERAL

  - The Contractor's attention is directed to the General and Special Conditions, General Conditions-Mechanical and to all other Contract Documents as they apply to this branch of the work.  Attention is also directed to all other sections of the Contract Documents which affect the work of this section and which are hereby made a part of the work specified herein.

  - Work under this section shall include all labor, equipment, accessories, materials and services required to furnish and install all insulation, fittings and finishes for all mechanical systems specified herein and/or as indicated.

  - Application of insulation materials shall be done in accordance with manufacturer's written recommendations.  Where thickness of insulation is not specified, use applicable thickness recommended by manufacturer for specific use.  Insulation shall be applied by a company regularly engaged in the application of insulation and any work deemed unacceptable by the Engineers shall be removed and properly installed at the expense of the Contractor.

- MANUFACTURERS

  - Insulation shall be as manufactured by Manville, Knauf, Owens-Corning, Armacell or other approved equivalent.  Insulation sundries and adhesives shall be as made by Benjamin Foster, Childers, Vimasco or approved equivalent.

- FIRE RATINGS AND STANDARDS

  - Insulations, jackets and facings shall have composite fire and smoke hazard ratings as tested by ASTM E-84, NFPA 255 and UL 723 procedures not exceeding Flame Spread 25, Smoke Developed 50.

  - Adhesives, mastics, tapes and fitting materials shall have component ratings as listed above.

  - All products and their packaging shall bear a label indicating above requirements are not exceeded.

- GENERAL APPLICATION REQUIREMENTS

  - Insulation shall be applied on clean, dry surfaces in a neat and workmanlike manner reflecting the best current practices in the trade.  Insulation shall not be applied to piping, ductwork or equipment until tested, inspected and released for insulation.

  - All insulation shall be continuous through walls, ceiling openings and sleeves.  However, insulation shall be broken through fire walls.  All covered pipe and ductwork is to be located a sufficient distance from walls, other pipe, ductwork and other obstacles to permit the application of the full thickness of insulation specified.  If necessary, extra fittings and pipe are to be used.  No noticeable deformation of insulation or discontinuity of vaporseal, where required, will be accepted.

  - "Concealed", where used herein, shall mean hidden from sight as in trenches, chases, furred spaces, pipe shafts, or above hung finished ceilings.  "Exposed" shall mean that piping or equipment is not "concealed" as defined above.  Piping and equipment in service tunnels, mechanical equipment rooms, storage areas, or unfinished rooms is to be considered as "exposed".

  - Existing and/or new insulation removed and/or damaged during course of construction shall be repaired or replaced as directed by the Engineer.

  - Vapor barrier jackets shall be applied with a continuous unbroken vapor seal.  Do not use staples thru the jacket.  NO EXCEPTIONS!

  - All insulation shall be installed with joints butted firmly together.

  - The Contractor shall insure that all insulation (piping, ductwork, equipment, etc.) is completely continuous along all conduits, equipment, connection routes, etc. carrying cold fluids (air, water, other) and that condensation can, in no way, collect in or on the insulation, equipment, conduits, etc.  Any such occurrence of condensation collection and/or damage therefrom shall be repaired solely at the expense of the Contractor.

- PIPING SYSTEMS

  - GENERAL

    - Bevel insulation and jacket at all points where insulation terminates at unions, flanges, valves and equipment.  Note:  Applies to hot water lines only; cold water lines require continuous insulation.

    - Pipe insulation shall extend around valve bodies to above drain pans in hydronic equipment over pumps, etc. to insure no condensation drip or collection.

    - Factory molded fittings may be installed in lieu of built-up fittings.  Jackets to be the same as adjoining insulation.  Insulated fittings must have same or better K factors than adjoining straight run insulation.

    - Valves, flanges and unions shall only be insulated when installed on piping whose surface temperature will be at or below the dew point temperature of the ambient air.

    - Insulation shall not extend through fire and smoke walls.  A UL-listed penetration system shall be used for each fire or smoke wall penetration in accordance with KBC.  Materials used such as caulk, sleeves, etc. shall be manufactured by 3M, Hilti, or equal.

  - INSULATION SHIELDS

    - Metal insulation shields are required at all pipe hangers where the piping is insulated.  Metal shields shall be constructed of galvanized steel, formed to a 180 degree arc.  Insulation shields shall be the following size:

| PIPE SIZE | SHIELD GAUGE | SHIELD LENGTH |
| --- | --- | --- |
| 2" AND LESS | 20 | 12" |
| 2 1/2" TO 4" | 18 | 12" |
| 5" TO 10" | 16 | 18" |
| 12" AND GREATER | 14 | 24" |

  - INSULATION MATERIAL (FOR THE FOLLOWING SYSTEMS)

Insulation shall be Owens-Corning Model 25ASJ/SSL or approved equivalent fiberglass pipe insulation with an all service jacket.  The insulation shall be a heavy density, pipe insulation with a K factor .23 at 75°F mean temperature.  The insulation shall be wrapped with a vapor barrier jacket.  The jacket shall have an inside foil surface with self sealing lap and a water vapor permeability of .02 perm/inch.  All circumferential joints shall be vapor sealed with butt strips.  All insulation shall be installed in strict accordance with the manufacturers’ recommendations.  The following pipes shall be insulated with the thickness of insulation as noted.

    - Domestic Cold Water

      - Piping 3’’ or less – use 1/2" thick insulation

    - Hydronic System Fill Lines From Domestic Cold Water - 1/2" thick.

    - Domestic 110F Hot Water and 110F Recirculating Hot Water.

      - Piping 1 ½’’ or less – use 1" thick insulation

      - Piping 2’’ or greater – use 2’’ thick insulation

    - Hydronic Hot Water or Geothermal. Geothermal Mains (HPS/HPR) are HDPE and not required to be insulated.  Branch piping may be copper.  All non-HDPE Geothermal piping shall be insulated.  Where a transition occurs, the insulation shall continue 6” beyond the end of the copper piping and onto the HDPE.

      - Piping 1 ½’’ or less – use 1" thick insulation

      - Piping 2’’ or greater – use 2’’ thick insulation

    - Horizontal Roof Leaders and Vertical Roof Leaders where exposed.

      - Piping 3’’ or less – use 1/2" thick insulation

      - Piping 4’’ or greater – use 1’’ thick insulation

    - Sanitary Sewer and plumbing fixture P-traps to waste stack – see schedule below.  Insulate horizontal runs which receive air conditioning condensate and which are not located below slab or grade.

      - Piping 3’’ or less – use 1/2" thick insulation

      - Piping 4’’ or greater – use 1’’ thick insulation

    - Condensate Drain Lines.

      - Piping 1 1/2’’ or less – use 1/2" thick insulation

      - Piping 2’’ or greater – use 1’’ thick insulation

  - JACKETS

    - Exposed (Mechanical Rooms or where piping is exposed such as no ceilings or ceiling clouds)

All insulated piping installed in the above areas shall have a canvas or PVC jacket up to 7 feet A.F.F.

      - 6 oz. canvas jacket with fire retardant lagging.  Apply to the insulation specified for the piping.

- DUCTWORK SYSTEMS

  - GENERAL

    - Duct sizes indicated are the net free area inside clear dimensions; where ducts are internally lined, overall dimensions shall be increased accordingly.

    - Duct insulation shall extend completely to all registers, grilles, diffusers, and louver outlets, etc., to insure no condensation drip or collection.  The backs of all supply diffusers, plenums, grilles, etc. shall be insulated only if indicated by details on the drawings.

    - All flexible duct connections on insulated ductwork shall be externally insulated.

  - EXTERNAL INSULATION

    - Supply Air

    - Outside Air from the Intake to OA-1

    - Exhaust/Relief Duct from OA-1 to the point of exhaust.

Owens/Corning, "Faced Duct Wrap - Type 150" or approved equivalent, 1-1/2" thick fiberglass duct wrap, 1-1/2 lb. density factory laminated to a reinforced foil kraft vapor barrier facing (FRK) with a 2" stapling flange at one edge.  Flame spread 24, smoke developed 50, vapor barrier performance 0.02 perms per inch.  K factor shall not exceed .26 at 75°F. mean temperature.

Note: Do not provide externally insulated duct per the above specification for any duct that is to be painted.  Insulated duct that is to be painted shall be dual wall ductwork per specification Section 231200, Sheet Metal and Flexible Duct.

- MECHANICAL EQUIPMENT

  - ROOF DRAIN SUMPS

    - Owens-Corning Model 475-FR or approved equivalent rigid board insulation with exterior vapor barrier jacket formed to bottom of sump basin.  Insulation shall have a K factor of .22 at 75F. mean temperature.  Insulation shall be 1" thick.  Insulation shall be formed to roof drain sump.  Vapor barrier shall remain continuous.

  - FLOOR DRAIN SUMPS (Applies to all Floor Drains which Receive Air Conditioning Condensate and which are Installed in Locations Other Than Slab on Grade)

    - Owens-Corning Model 475-FR or approved equivalent rigid board insulation with exterior vapor barrier jacket formed to bottom of sump basin.  Insulation shall have a K factor of .22 at 75F. mean temperature.  Insulation shall be 1" thick.  Insulation shall be formed to roof drain sump.  Vapor barrier shall remain continuous.

  - EXPANSION TANK, COMPRESSION TANK, AIR SEPARATOR, LOOP FILLERS

    - Owens-Corning "Tank Wrap I" or approved equivalent.  Insulation shall be constructed of non-combustible, flexible wool.  Insulation shall be 2" thick.  K factor shall be .29 at 100F. mean temperature.  Insulation shall be attached in strict accordance with the manufacturer’s recommendations.  All insulation shall be jacketed with 6 oz. canvas with fire retardant lagging.  Coordinate with mechanical contractor to extend all piping connections, blowdown ports, etc. outside of the insulation.  Additionally for loop filters and other equipment requiring periodic service, provide removable insulated covers.

END OF SECTION INSULATION