SECTION 230200 - HVAC EQUIPMENT AND HYDRONIC SPECIALTIES

- GENERAL

  - The Contractor's attention is directed to the General and Special Conditions, General Conditions-Mechanical and to all other Contract Documents as they apply to this branch of the work.  Attention is also directed to all other sections of the Contract Documents which affect the work of this section and which are hereby made a part of the work specified herein.

  - The Contractor shall provide in complete working order the following heating, ventilation and air conditioning equipment located as indicated and installed, connected and placed in operation in strict accordance with the manufacturer's recommendations.  All equipment shall be factory painted and, where applicable, factory insulated and shall, where such standards exist, bear the label of the Underwriters Laboratory.

  - Each subcontractor shall be responsible for their own completion of System Verification Checklists/Manufacturer’s Checklist.

  - Factory startup is required for all HVAC equipment.  In general, as part of the verification process, equipment suppliers shall perform start-up by their factory authorized technicians and shall complete and submit start-up reports/checklists.  This shall include heat pumps, chillers, VFDs, air handling units, etc.

  - All HVAC equipment shall comply with the latest provisions of ASHRAE Standard 90 and/or International Energy Conservation Code 2006, whichever is more stringent.

  - Installation of all heating, ventilating and air conditioning systems shall be performed by a master HVAC contractor licensed in the state the work will be performed.

  - Note to Suppliers and Manufacturers Representative furnishing proposals for equipment for the project:

    - Review the Controls Section of these Specifications (if applicable) to determine controls to be furnished by the equipment manufacturer, if any.  The Contractor shall provide all controls with equipment unless specifically listed otherwise.

    - Review the section of these specifications entitle:  REQUIRED SHOP DRAWINGS, DESCRIPTIVE LITERATURE, MAINTENANCE  MANUALS, PARTS LISTS, SPECIAL KEYS, TOOLS, ETC., and provide all documents called for therein.

    - Insure that the equipment which you propose to furnish may be installed, connected, placed in operation and easily maintained at the location and in the space allocated for it.

    - Determine from the Bid Documents the date of completion of this project and insure that equipment delivery schedules can be met so as to allow this completion date to be met.

    - Where manufacturers’ temperature controls are specified, they shall be in full compliance with International Mechanical Code Section 606 including automatic smoke shut down provisions.

    - Provide factory start-up on site by a factory representative (not a third party contractor) for all HVAC equipment, including pumps, VFDS, boilers, chillers, cooling towers, heat pumps, rooftop units, etc.  Submit factory start-up reports to the Engineer.

    - Provide training to the Owner by a factory representative for each type of equipment.  Refer to the Training requirements, 017900, within the front end specifications for further requirements.

    - Review the Section on Motor Starters and Electrical Requirements for Mechanical Equipment.

    - Requirements for motors controlled by variable frequency drives:

      - All motors shall be inverter duty rated.

      - Motors 5 HP to 100 HP in size shall be furnished with shaft grounding kit, Aegis SGR Bearing Protection Ring or equal.  One shaft grounding ring and related hardware shall be provided on drive end or non-drive end of motor per manufacturer’s instructions.  Ground motor frame per manufacturer’s instructions.  Install kit in strict accordance with manufacturer’s instructions.

    - All condensate producing equipment shall be provided with a condensate trap as recommended by the equipment manufacturer and a condensate overflow switch where applicable such as heat pumps.

    - Provide low ambient and all required controls and accessories on all HVAC equipment to ensure they can provide cooling during the winter season.

    - Provide a complete air tight enclosure with opening door that seals air tight for all filters on air moving equipment.

    - All equipment shall be furnished for a single point electrical connection unless specifically excluded as a requirement.

- EQUIPMENT

  - OUTSIDE AIR UNIT (OA-1) - General

AFBMA 9 - Load Ratings and Fatigue Life for Ball Bearings.

AMCA 99 - Standards Handbook.

AMCA 210 - Laboratory Methods of Testing Fans for Rating Purposes.

AMCA 300 - Test Code for Sound Rating Air Moving Devices.

AMCA 500 - Test Methods for Louver, Dampers, and Shutters.

ARI 410 - Forced-Circulation Air-Cooling and Air-Heating Coils.

ARI 430 - Central-Station Air-Handling Units.

ARI 435 - Application of Central-Station Air-Handling Units.

ASTMB117 -  Standard Practice for Operating Salt Spray Apparatus.

NEMA MG1 - Motors and Generators.

NFPA 70 - National Electrical Code.

SMACNA - HVAC Duct Construction Standards - Metal and Flexible.

UL 723 - Test for Surface Burning Characteristics of Building Materials.

UL 900 - Test Performance of Air Filter Units.

UL 1995 - Standard for Heating and Cooling Equipment.

UL 94 - Test for Flammability of Plastic Materials for Parts in Devices and Appliances.

IBC 2000, 2003 - International Building Code.

NFPA 90A - Standard for the Installation of Air Conditioning and Ventilating Systems.

NFPA 5000 - Building Construction and Safety Code.

ASHRAE 90.1 Energy Code.

ARI Standard 1060 - Rating Air-to-Air Heat Exchangers for Energy Recovery Ventilation Equipment.

GSA 2003 Facilities Standard - 5.9 HVAC Systems and Components.

  - SUBMITTALS

    - Shop Drawings: Indicate assembly, unit dimensions, weight loading, required clearances, construction details, field connection details, and electrical characteristics and connection requirements. Computer generated fan curves for each air handling unit shall be submitted with specific design operating point noted. A computer generated psychometric chart shall be submitted for each cooling coil with design points and final operating point clearly noted. Sound data for discharge, radiated and return positions shall be submitted by octave band for each unit. Calculations for required baserail heights to satisfy condensate trapping requirements of cooling coil shall be included.

    - Product Data:

      - Provide literature that indicates dimensions, weights, capacities, ratings, fan performance, finishes of materials, electrical characteristics, and connection requirements.

      - Provide data of filter media, filter performance data, filter assembly, and filter frames.

      - Provide manufacturer's installation instructions.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing Air Handler products specified in this section must show a minimum five years documented experience and complete catalog data on total product.

  - SAFETY AGENCY LISTED & CERTIFICATION

    - Air handling units shall be cETLus safety listed to conform with UL Standard 1995 and CAN/CSA Standard C22.2 No. 236.

    - Air handling unit water heating & cooling coils shall be certified in accordance with the forced circulation air cooling and air heating coils certification program, which is based on ARI Standard 410.

  - DELIVERY, STORAGE, AND HANDLING

    - Deliver, store, protect and handle products to site.

    - Accept products on site on factory-furnished shipping skids.  Inspect for damage.

    - Store in clean dry place and protect from construction traffic. Handle carefully to avoid damage to components, enclosures, and finish.

- PRODUCTS

  - The following manufacturers are approved for use:

    - McQuay 'Vision' Air Handler shall be the basis of design.

    - Semco - VS Series

    - Trane - Performance Climate Changer

      - GENERAL DESCRIPTION

        - Configuration: Fabricate as detailed on drawings.

        - Performance: Conform to ARI 430.  See schedules on drawings.

      - UNIT CONSTRUCTION

        - Fabricate unit with heavy gauge channel posts and panels secured with mechanical fasteners.  All panels, access doors, and ship sections shall be sealed with permanently applied bulb-type gasket.  Shipped loose gasketing is not allowed.

        - Panels and access doors shall be constructed as a 2-inch nominal thick; thermal broke double wall assembly, injected with foam insulation with an R-value of not less than R-13.

          - The inner liner shall be constructed of G90 galvanized steel.

          - The outer panel shall be constructed of G90 galvanized steel.

          - The floor plate shall be constructed as specified for the inner liner.

          - Unit will be furnished with solid inner liners.

        - Panel deflection shall not exceed L/240 ratio at 125% of design static pressure, maximum 5 inches of positive or 6 inches of negative static pressure.  Deflection shall be measured at the panel midpoint.

        - The casing leakage rate shall not exceed .5 cfm per square foot of cabinet area at 5 inches of positive static pressure or 6 inches of negative static pressure (.0025 m3/s per square meter of cabinet area at 1.24 kPa static pressure).

        - Module to module field assembly shall be accomplished with an overlapping, full perimeter internal splice joint that is sealed with bulb type gasketing on both mating modules to minimize on-site labor and meet indoor air quality standards.

        - Access doors shall be flush mounted to cabinetry, with minimum of two six inch long stainless steel piano-type hinges, latch and full size handle assembly.  Access doors shall swing outward for unit sections under negative pressure. Access doors on positive pressure sections, shall have a secondary latch to relieve pressure and prevent injury upon access.

        - A 4-inch formed G60 galvanized steel base rail shall be provided by the unit manufacturer for structural rigidity and condensate trapping.  The base rail shall be constructed with 10-gauge nominal for unit sizes 040 - 090.

        - Construct drain pans from microbial resistant coated galvanized steel with cross break and double sloping pitch to drain connection.  Provide drain pans under cooling coil section.  Drain connection centerline shall be a minimum of 3’’ above the base rail to aid in proper condensate trapping.  Drain connections that protrude from the base rail are not acceptable.  There must be a full 2’’ thickness of insulation under drain pan.

      - FAN ASSEMBLIES

        - Fan and motor shall be mounted internally on a steel base.  Factory mount motor on slide base that can be slid out the side of the unit if removal is required.  Provide access to motor, drive, and bearings through hinged access door.  Fan and motor assembly shall be mounted on 2" deflection spring vibration type isolators inside cabinetry.

      - BEARINGS, SHAFTS, AND DRIVES

        - Bearings:  Basic load rating computed in accordance with AFBMA - ANSI Standards.  The bearings shall be designed for service with an L-50 life of 200,000 hours and shall be a heavy duty pillow block, self-aligning, grease-lubricated ball or spherical roller bearing type.

        - Shafts shall be solid, hot rolled steel, ground and polished, keyed to shaft, and protectively coated with lubricating oil. Hollow shafts are not acceptable.

        - V-Belt drives shall be cast iron or steel sheaves, dynamically balanced, bored to fit shafts and keyed.  Fixed sheaves, matched belts, and drive rated based on motor horsepower.  Standard drive service factor minimum shall be 1.1 S.F. for 1/4 HP – 7.5 HP, calculated based on fan brake horsepower.

      - ELECTRICAL

        - Fan motors shall be manufacturer provided and installed, Open Drip Proof, premium efficiency (meets or exceeds EPAct requirements), 1750 RPM, single speed, 460V / 60HZ / 3P.  Complete electrical characteristics for each fan motor shall be as shown in schedule.

        - The air handler(s) shall be ETL and ETL-Canada listed by Intertek Testing Services, Inc. Units shall conform to bi-national standard ANSI/UL Standard 1995/CSA Standard C22.2 No. 236.

        - Wiring Termination: Provide terminal lugs to match branch circuit conductor quantities, sizes, and materials indicated.  Enclosed terminal lugs in terminal box sized to NFPA 70.

        - Manufacturer shall provide ASHRAE 90.1 Energy Efficiency equation details for individual equipment to assist Building Engineer for calculating system compliance.

        - Refer to motor specification for additional requirements.

      - COOLING AND HEATING COILS

        - Certification: Acceptable water cooling and water heating, coils shall be certified in accordance with ARI Standard 410 and bear the ARI label.  Coils exceeding the scope of the manufacturer’s certification and/or the range of ARI’s standard rating conditions will be considered provided the manufacturer is a current member of the ARI Forced Circulation Air-Cooling and Air-Heating Coils certification programs and that the coils have been rated in accordance with ARI Standard 410.  Manufacturer must be ISO 9002 certified.

        - Water cooling coil shall be provided.  Provide access to coil(s) for service and cleaning.  Enclose coil headers and return bends fully within unit casing.  Unit shall be provided with coil connections that extend a minimum of 5” beyond unit casing for ease of installation.  Drain and vent connections shall be provided exterior to unit casing.  Coil connections must be factory sealed with grommets on interior and exterior panel liners to minimize air leakage and condensation inside panel assembly. If not factory packaged, Contractor must supply all coil connection grommets and sleeves. Coils shall be removable through side and/or top panels of unit without the need to remove and disassemble the entire section from the unit.

        - Headers shall consist of seamless copper tubing to assure compatibility with primary surface.  Headers to have intruded tube holes to provide maximum brazing surface for tube to header joint, strength, and inherent flexibility.  Header diameter should vary with fluid flow requirements.

        - Fins shall have a minimum thickness of 0.0075 inch aluminum plate construction. Fins shall have full drawn collars to provide a continuous surface cover over the entire tube for maximum heat transfer.  Tubes shall be mechanically expanded into the fins to provide a continuous primary to secondary compression bond over the entire finned length for maximum heat transfer rates.  Bare copper tubes shall not be visible between fins.

        - Coil tubes shall be 5/8 inch OD seamless copper, 0.024 inch nominal tube wall thickness, expanded into fins, brazed at joints. Soldered U-bends shall be provided to minimize the effects of erosion and premature failure having a minimum tube wall thickness of .025 inches.

        - Coil connections shall be carbon steel, NPT threaded connection.  Connection size to be determined by manufacturer based upon the most efficient coil circuiting.  Vent and drain fittings shall be furnished on the connections, exterior to the air handler.  Vent connections provided at the highest point to assure proper venting.  Drain connections shall be provided at the lowest point to insure complete drainage and prevent freeze-up.

        - Coil casing shall be a formed channel frame of galvanized steel.

      - FILTERS

        - Furnish angled filter in mixing box section with 2-inch MERV 13 filter.  Provide side loading and removal of filters.

        - Filter media shall be UL 900 listed, Class I or Class II.

        - Filter Magnehelic gauge(s) shall be furnished and mounted by others.

      - ADDITIONAL SECTIONS

        - Access section shall be provided for access between components.

        - Face and bypass section shall be provided to modulate airflow through and around heat transfer coils. Dampers shall be an integral part of the unit assembly.  Internal face and top bypass shall be contained in the standard cabinet height. Blank-off and division sheets, internal linkage, access doors installed by unit manufacturer.  Face and bypass dampers shall be of low leak design, opposed blade, with vinyl bulb edging and stainless steel edge seals, galvanized steel frame and axles in self-lubricating nylon bearings.

        - Mixing box section shall be provided with end outside air opening and no return air opening with or without parallel low leak airfoil damper blades.  Dampers shall be hollow core galvanized steel airfoil blades, fully gasketed and have continuous vinyl seals between damper blades in a galvanized steel frame.  Dampers shall have stainless steel jamb seals along end of dampers.  Connecting linkage and ABS plastic end caps shall be provided when return and outside air dampers are each sized for full airflow.  Return and outside air dampers of different sizes must be driven separately.  Damper Leakage: Leakage rate shall be less than two tenths of one percent leakage at 2 inches static pressure differential.  Leakage rate tested in accordance with AMCA Standard 500.

        - Mixing box section shall be provided with no outside air opening and end return air opening with or without parallel low leak airfoil damper blades.  Dampers shall be hollow core galvanized steel airfoil blades, fully gasketed and have continuous vinyl seals between damper blades in a galvanized steel frame.  Dampers shall have stainless steel jamb seals along end of dampers.  Linkage and ABS plastic end caps shall be provided when return and outside air dampers sized for full airflow.  Return and outside air dampers of different sizes must be driven separately.  Damper Leakage: Leakage rate shall be less than two tenths of one percent leakage at 2 inches static pressure differential.  Leakage rate tested in accordance with AMCA Standard 500.

        - Energy recovery wheel shall be constructed of corrugated synthetic fibrous media, with a desiccant intimately bound and uniformly and permanently dispersed throughout the matrix structure of the media.  Rotors with desiccants coated bonded, or synthesized onto the media are not acceptable due to delaminating or erosion of the desiccant material.  Media shall be synthetic to provide corrosion resistance and resistance against attack from laboratory chemicals present in pharmaceutical, hospital, etc. environments as well as attack from external outdoor air conditions.  Coated aluminum is not acceptable.  Face flatness of the wheel shall be maximized in order to minimize wear on inner seal surfaces and to minimize cross leakage.  Rotor shall be constructed of alternating layers of flat and corrugated media.  Wheel layers should be uniform in construction forming uniform aperture sizes for airflow.   Wheel construction shall be fluted or formed honeycomb geometry so as to eliminate internal wheel bypass.  Wheel layers that can be separated or spread apart by airflow are unacceptable due to the possibility of channeling and performance degradation.  The minimum acceptable performance shall be as specified in the unit schedule.

        - Desiccant Material: The desiccant material shall be a molecular sieve, and specifically a 4A or smaller molecular sieve to minimize cross contamination. Wheel Media Support System: The wheel frames shall consist of evenly spaced steel spokes, galvanized steel outer band and rigid center hub.  The wheel construction should allow for post fabrication wheel alignment. Wheel Seals: The wheel seals shall be full contact nylon brush seals or equivalent.  Seals should be easily adjustable. Wheel cassette: Cassettes shall be fabricated of heavy duty reinforced galvanized steel or welded structural box tubing.  Cassettes shall have a built in adjustable purge section minimizing cross contamination of supply air as shown on unit schedule.  Bearings shall be inboard, zero maintenance, permanently sealed roller bearings, or alternatively, external flanged or pillow block bearings.   Drive systems shall consist of fractional horsepower AC drive motors with multi-link drive belts. Face and bypass dampers shall be furnished as shown on unit schedule and drawings. Certification:  The wheel shall be ARI certified by the energy recovery wheel supplier to ARI Standard 1060 and must bear the ARI certification stamp.  Private independent testing performed "in accordance with" various standards is not a substitute for ARI certification and shall not be accepted.  The wheel shall be listed or recognized by UL or equivalent.

  - 2 STAGE WATER SOURCE HEAT PUMPS (Geothermal Extended Range)

    - All equipment shall be ARI Certified per ARI/ISO/ASHRAE/ANSI Standard 13256-1 for Group Loop Rating.  All units shall be UL Listed for product safety.  All units shall have ARI13256-1 and UL labels.  Units shall be designed to operate throughout the range of entering fluid temperature of 25ºF to 110ºF.  The system is 100% water and freezestats shall be adjustable from 40 deg to 60 deg F on entering water temperature.

      - Acceptable Manufacturers are McQuay, ClimateMaster, JCI, FHP, or Trane.

      - To be considered equivalent, a manufacturer must submit a calculated system EER and be no less than 95% of the basis of design System EER.   Satisfying this requirement does not alleviate the manufacturer from complying with all other specified requirements and performance data. To calculate the System EER, utilize the following equation with each size heat pump on the project included:

System EER= ((Quantity of Smallest capacity HP x Scheduled EER)+….+(Quantity of Largest capacity HP x Scheduled EER))/Total Number of  WSHP’s.

    - BASIC CONSTRUCTION

      - Units shall have the air flow arrangement as shown on the plans.  The heat pumps shall be fabricated from heavy gauge galvalume sheet metal coated with lacquer acrylic.  All interior surfaces shall be lined with ½ inch, 1-1/2 lb. acoustic type glass fiber insulation.  All fiberglass insulation shall be coated and shall meet NFPA 90A.  Units shall have a factory installed filter bracket for use with standard 1-inch filters.  Supply and return water connections shall be copper FPT fittings and shall be securely mounted flush to the cabinet allowing for connection to a flexible hose without the use of a back-up wrench.  All units shall have a stainless steel drain pan.

    - FAN AND MOTOR ASSEMBLY

      - All units shall have a direct-drive centrifugal fan.  The fan motor shall be variable speed, permanently lubricated, ECM type with thermal overload protection.  The fan motor shall be isolated from the fan housing by torsionally flexible isolation.  The fan motor shall vary the speed of the fan to maintain a constant airflow quantity.  External static pressure rating of the unit shall be based on a wet coil.

    - REFRIGERANT CIRCUIT

      - Units shall have a sealed, R-410A, refrigerant circuit including a two-stage hermetic scroll compressor, thermal expansion valve, finned tube refrigerant-to-air heat exchanger, a reversing valve, a coaxial (tube-in-tube) refrigerant-to-water heat exchanger, and safety controls including a high pressure switch and a low pressure switch.  The reversing valve shall be a four-way solenoid activated on a call for cooling, which fails to the heating position.  Access fittings shall be factory installed on high and low pressure refrigerant lines to facilitate field service.  Activation of any safety device shall prevent compressor operation via a lockout circuit.  The lockout circuit shall allow reset at the thermostat or at the disconnect switch or through the DDC.  Hermetic scroll compressors with internal overload protection shall be mounted on rubber isolators and be located in an insulated compartment to minimize sound transmission.

      - The two stage hermetic scroll compressor shall be activated via a 2-stage control system.  Stage one shall activate the part load capacity of the compressor for operation at approximately 70% of full load capacity.  The ECM fan motor shall automatically reduce the fan speed to maintain a constant airflow quantity at approximately 70% of the full load air quantity.  Stage two shall activate the full load capacity of the compressor and the ECM fan motor.

    - ELECTRICAL

      - A control box shall be located within the unit and shall contain a printed circuit UPM control board, 50VA transformer, controls for compressor, reversing valve, condensate safety sensor and fan motor.  Each unit shall have a terminal block for low voltage field wiring connections.  Unit controls shall be 24 volts and shall provide heating or cooling as required by the wall thermostat.

      - The unit-mounted UPM control system shall have the following features:

        - Anti-short cycle time delay on compressor operation.

        - Random start on power up mode.

        - High and low voltage interruption protection.

        - 90-second bypass timer for the low pressure switch.

        - Shutdown on high or low refrigerant pressure switch, freezestat or condensate sensor.

        - Alarm output which closed for remote fault indication.

        - Reset of a unit safety switch at the wall thermostat or at the main power disconnect.

        - Automatic intelligent reset.  Unit shall automatically reset the unit one time after a safety shut down.

        - Ability to defeat time delays for servicing.

        - A LED to indicate safety alarms.  The LED shall annunciate the following alarms:  high refrigerant pressure, low refrigerant pressure, low water temperature, or a high level of condensate in the drain pan.

    - PIPING:

      - Each unit shall supply, return water and condensate drain connections shall be copper or brass female pipe thread fittings and mounted flush to cabinet exterior.

  - WATER TO WATER HEAT PUMP  (Geothermal Extended Range)

    - General:

      - Furnish and install water-source heat pumps as indicated on the plans and listed in the unit schedule. All units must be factory run tested in the heating with full water flow. All equipment must be certified for capacity and efficiency by ARI and be safety agency listed with ETL.

    - Unit Construction:

      - The outer casing and internal support parts shall be fabricated from G-60 galvanized steel. All interior metal parts exposed to moisture and cold temperatures shall be insulated with acoustic-type, 3/4-inch, 1.5 pound, skin-coated fiberglass.

    - Unit Electrical:

      - The unit shall have single point power and provide protection against single phase, phase imbalance and low voltage conditions.

    - Water Connections:

      - Supply and return water connections shall have male NPT copper fittings located outside the cabinet for connection to flexible hoses.

    - Refrigeration System:

      - Each unit shall have a minimum of two separate circuits complete with scroll compressor, thermal expansion valve with external equalizer line and is serviceable and adjustable while the unit is in operation. Units shall be designed for use of R-410A refrigerant. Water source heat pump units shall include a reversing valve. The reversing valve is energized in the cooling mode and is fail-safe to the heating mode. Each circuit is equipped with low and high pressure refrigerant manual reset safety controls, Schrader valves on both the high and low pressure sides and liquid line filter drier.. Each refrigerant circuit shall be fully charged and ready for operation, requiring only connection of water and electrical services.  Compressors shall be scroll type with thermal overload protection.  Compressors shall be scroll compressors with a minimum of two compressors per unit to provide staging.  Compressors shall be mounted in an isolated service compartment that can be accessed without affecting unit operation. Compressors shall be isolated from unit with rubber vibration isolators. Unit shall incorporate brazed plate heat exchangers made of stainless steel and copper with built in DX distributors for maintaining proper balanced flows. Refrigerant side is rated for 650 PSI. Field piping connections shall be MPT connections and shall be made to each heat exchanger at the top of the unit and incorporate isolation valves and manual drain valves as standard equipment. The refrigeration circuit(s) shall have a 5 year NON-Prorated parts warranty, including the compressor(s), heat exchanger(s), reversing valve(s) thermal expansion valve(s).The unit shall be rated for low temperature (geothermal) applications.  All warranties begin at substantial completion.

    - Heat Exchangers:

      - The water-to-refrigerant heat exchangers shall be flat plate design with copper and stainless steel plates and rated at 650 psig on the refrigerant side and 450 psig on the water side. Safety controls include a high refrigerant pressure switch and a low refrigerant pressure switch for protection against loss of charge and extreme low temperature operation. Unit shall have factory mounted flow switches on both load and source sides. Each unit shall be capable of starting with 40° F entering water source side temperature and 110°F load side temperature in the heating mode.  Freezestats shall be adjustable from 40 deg F to 60 deg F entering water temperature.

    - Controls:

      - The DDC controller shall be field installed building controls shall be BACnet.

  - HOSE KITS

    - Hose kit sizes shall be as scheduled on the drawings.

      - Provide a factory-assembled, one piece hose kit/piping package for supply and return connections for each heat pump.

      - Contractor shall provide and install Hays Hose Kit Piping Packages or Nexus Hose Kit Piping packages with integral automatic balance valve. Each kit shall be sized for 2.0 to 7.0 feet per second.  Valves may be mounted in any altitude and do not require straight sections of pipe either upstream or down stream for proper operation.

      - Each return side hose kit/piping package shall include the following:

        - Single piece Y - valve body for sizes ½” – 1-1/2”, shall be constructed of hot forged brass with threaded inlets and outlets.  2” – 3” shall be constructed of bronze.  All valve bodies are suitable for a minimum of 400 PSIG working pressure.

        - Automatic flow control valves shall be factory set to rated flow and shall automatically control the flow to within 10% of the rated value subject to the operating parameters of; 2 to 80 PSID, fluid freezing to 225° F, 2.0 to 7.0 FPS.

        - Valve internal control mechanism shall be of a quiet, clog resistant design with reverse flow capabilities and consist of precision orifice that is field changeable within the listed flow rate.

        - Single pressure/temperature test ports for verifying the pressure differential and system temperature, full flow design ball valve with blow out proof stems for shut off.

        - Manufacturer shall provide certified independent laboratory tests verifying accuracy of performance.

        - All valves shall be labeled with controlled flow direction, flow rate, PSID control range, manufacturer and model number, unit tagging.

      - Each supply side hose kit/piping package shall include the following:

        - Single piece Y - valve body for sizes ½” – 1-1/2”, shall be constructed of hot forged brass with threaded inlets and outlets. 2-3” shall be constructed of bronze.  4” and larger shall be constructed of carbon steel with flanged inlets and outlets.  All valve bodies are suitable for a minimum of 400 PSIG working pressure.

        - Single pressure/temperature test ports for verifying the pressure differential and system temperature, full flow design ball valve with blow out stems for shut off.

        - Strainer shall be Y-type configuration furnished with hose connector blow down valve.  Strainer screen shall be stainless steel mesh and easily accessible for cleaning without disconnecting hoses.

        - All valves shall be labeled with flow direction, manufacturer and model number, unit tagging.

      - Stainless Steel Braided Supply and Return Hoses:  All hoses shall be equipped with end connections at terminal unit.  All end connections shall be either permanently crimped swivel ends or butt welded to carbon steel end fittings to meet stated pressure ratings.  Operational temperature shall be rated from fluid freezing to 200 degrees F. Minimum burst pressure shall be four times the working pressure.  Furnish with field flushing connection fitting. ½” to 1-1/4” shall be reinforced, fire retardant EPDM rubber, bonded to the inside wall of braiding.  1 ½” and larger shall be a corrugated type 321 stainless steel tube.

      - Flushing Bypass:  Provide with means at each heat pump to flush system completely while allowing no fluid flow through heat pump.  Also see “Start-up and Flushing” instructions in this section.

      - Condensate Hose Kits:  Contractors Option:  Manufactured ¾” tubing x 54” long clear flexible plastic hose, with molded P-trap, fittings, couplings and clamps.  All condensate drains larger than ¾” shall be field fabricated by contractor to allow for flexible movement.  All sizes shall match sizes indicated on drawings.

      - Warranty:  Automatic Flow Control Valves containing orifice and diaphragm shall be warranted for the life of the HVAC system in which it was originally installed.  Manufacturer shall warrant all other components, for no less than five (5) years from Substantial Completion.  Manufacturer shall warrant steel braided hose for no less than three (3) years from date of substantial completion.

  - HEAT PUMP AIR FILTER SYSTEM FOR VERTICAL HEAT PUMP UNITS

(1)	GENERAL: The Contractor shall completely assemble each system for each heat pump and install in heat pumps ready to use.

Heat pumps 5 tons and smaller require one 24” X 24” air filter system (one 24 x 24 filter).

Heat pumps 6 tons through 10 tons require one 48” x 24” air filter system (two 24 x 24 filters).

These dimensions are typical unless noted otherwise on the drawings.

(2)	Side Access Filter Housing:

Airguard single stage flat bank side access filter housing (Model FB).

Accommodate required quantity of 24” x 24” x 2” deep flat filters.

Factory assembled.

One door.

16 gauge aluminized steel.

See plans for sizes and quantities per unit.

(3)	Filter Media:

AAF, 2” thick pleated, MERV 13 filters.

  - Ventilating Fans

    - Ventilating fans shall be of the type, capacity, size, etc. here-in-after scheduled.  Catalog numbers are listed as design criteria only.  Alternate selections will be accepted provided quality, function, etc. are equivalent.  All fans shall be UL listed, complete with all required disconnects and starters and shall be AMCA rated and certified.  Model numbers listed are Greenheck, acceptable alternates are Penn, Carnes, Acme, Shipman, Jenn-Aire and Loren-Cook.  The Architect shall select the color for all exposed fans.

    - Selection

Refer to the schedule on the plans.

  - Combination Variable Frequency Drive / Disconnect (Vfd) For Motors 50 Hp And Less

    - Manufacturers

      - Danfoss Graham VLT 6000 Series, Reliance, Yaskawa, Emerson, ABB, or approved equal.

    - General

      - Furnish complete variable frequency VFDs as specified herein for the fans and pumps designated on the drawing schedules to be variable speed.  All standard and optional features shall be included within the VFD enclosure, unless otherwise specified.  VFD shall be housed in a metal NEMA enclosure of type according to the installation and operating conditions at the job site.  The VFD’s UL listing shall allow mounting in plenum or other air handling compartments. If a NEMA 12 enclosure is required for the plenum rating, the manufacturer must supply a NEMA 12 rated VFD.

      - The VFD shall have integral disconnecting means to disconnect power to device in accordance with NEC.

      - The VFD shall convert incoming fixed frequency three-phase AC power into a variable frequency and voltage for controlling the speed of three-phase AC motors.  The motor current shall closely approximate a sine wave.  Motor voltage shall be varied with frequency to maintain desired motor magnetization current suitable for centrifugal pump and fan control and to eliminate the need for motor derating.

      - With the motor’s rated voltage applied to the VFD input, the VFD shall allow the motor to produce full rated power at rated amps, RMS fundamental volts, and speed without using the motor’s service factor. VFDs utilizing sine weighted/coded modulation (with or without 3rd  harmonic injection) must provide data verifying that the motors will not draw more than full load current during full load and full speed operation.

      - The VFD shall include an input full-wave bridge rectifier and maintain a fundamental power factor near unity regardless of speed or load.

      - The VFD and options shall be tested to ANSI/UL Standard 508.  The complete VFD, including all specified options, shall be assembled by the manufacturer, which shall be UL-508 certified for the building and assembly of option panels. Assembly of the option panels by a third-party panel shop is not acceptable.  The appropriate UL stickers shall be applied to both the VFD and option panel, in the case where these are not contained in one panel. When these VFDs are to be located in Canada, CSA or C-UL certifications shall apply.  Both VFD and option panel shall be manufactured in ISO 9001 certified facilities.

      - The VFD shall have a dual 5% DC link reactor on the positive and negative rails of the DC bus to minimize power line harmonics and protect the drive from power line transients.  The reactor shall be non-saturating (linear) to provide full harmonic filtering throughout the entire load range.  VFDs with saturating (non-linear) DC link reactors shall require an additional 3% AC line reactor to provide acceptable harmonic performance at full load, where harmonic performance is most critical.

      - The VFD’s full load amp rating shall meet or exceed NEC Table 430-150.  The VFD shall be able to provide full rated output current continuously, 110% of rated current for 60 seconds and 160% of rated current for up to 0.5 second while starting.

      - The VFD shall be able to provide full torque at any selected frequency from 29 Hz to base speed to allow driving direct drive fans without derating.

      - An automatic energy optimization selection feature shall be provided standard in the VFD.  This feature shall automatically and continually monitor the motor’s speed and load and adjust the applied voltage to maximize energy savings and provide up to an additional 3% to 10% energy savings.

      - Input and output power circuit switching shall be able to be accomplished without interlocks or damage to the VFD.  Switching rate may be up to 1 time per minute on the input and unlimited on the output.

      - An automatic motor adaptation test algorithm shall measure motor stator resistance and reactance to optimize performance and efficiency.  It shall not be necessary to run the motor or de-couple the motor from the load to run the test.

      - Galvanic and/or optical isolation shall be provided between the VFD’s power circuitry and control circuitry to ensure operator safety and to protect connected electronic control equipment from damage caused by voltage spikes, current surges, and ground loop currents.  VFDs not including either galvanic or optical isolation on both analog I/O and discrete I/O shall include additional isolation modules.

      - VFD shall minimize the audible motor noise through the used of an adjustable carrier frequency.  The carrier frequency shall be automatically adjusted to optimize motor and VFD efficiencies while reducing motor noise.

      - VFD supplier shall coordinate with motor supplier to ensure that all motors 20 horsepower and greater are provided with grounding bushings.

    - Protective Features

a.	A minimum of Class 20 I2t electronic motor overload protection for single motor applications and thermal-mechanical overloads for multiple motor applications shall be provided.

b.	Protection against input transients, loss of AC line phase, output short circuit, output ground fault, overvoltage, undervoltage, VFD overtemperature and motor overtemperature.  The VFD shall display all faults in plain English. Codes are not acceptable.

c.	Protect VFD from sustained power or phase loss.  The VFD shall provide full rated output with an input voltage as low as 90% of the nominal.  The VFD will continue to operate with reduced output with an input voltage as low as 164 V AC for 208/230 volt units, 313 V AC for 460 volt units, and 394 volts for 600 volts units.

d.	The VFD shall incorporate a motor preheat circuit to keep the motor warm and prevent condensation build up in the stator.

e.	VFD package shall include semi-conductor rated input fuses to protect power components.

f.	To prevent breakdown of the motor winding insulation, the VFD shall be designed to comply with IEC Part 34-17.  Otherwise the VFD manufacturer must ensure that inverter rated motors are supplied.

g.	VFD shall include a “signal loss detection” circuit to sense the loss of an analog input signal such as 4 to 20 mA or 2 to 10 V DC, and shall be programmable to react as desired in such an instance.

h.	VFD shall function normally when the keypad is removed while the VFD is running and continue to follow remote commands.  No warnings or alarms shall be issued as a result of removing the keypad.

i.	VFD shall catch a rotating motor operating forward or reverse up to full speed.

j.	VFD shall be rated for 100,000 amp interrupting capacity (AIC).

k.	VFD shall include current sensors on all three output phases to detect and report phase loss to the motor.  The VFD will identify which of the output phases is low or lost.

l.	VFD shall continue to operate without faulting until input voltage reaches 300 V AC on 208/230 volt units, 539 V AC on 460 volt units, and 690 volts on 600 volt units.

    - Interface Features

a.	Hand/Start, Off/Stop and Auto/Start selector switches shall be provided to start and stop the VFD and determine the speed reference.

b.	The VFD shall be able to be programmed to provide a 24 V DC output signal to indicate that the VFD is in Auto/Remote mode.

c.	The VFD shall provide digital manual speed control. Potentiometers are not acceptable.

d.	Lockable, alphanumeric backlit display keypad can be remotely mounted up to 10 feet away using standard 9-pin cable.

e.	The keypads for all sizes of VFDs shall be identical and interchangeable.

f.	To set up multiple VFDs, it shall be possible to upload all setup parameters to the VFD’s keypad, place that keypad on all other VFDs in turn and download the setup parameters to each VFD.  To facilitate setting up VFDs of various sizes, it shall be possible to download from the keypad only size independent parameters.

g.	Display shall be programmable to display in 9 languages including English, Spanish and French.

h.	The display shall have four lines, with a minimum of  20 characters on three lines and a minimum of eight large characters on one line.

i.	A red FAULT light, a yellow WARNING light and a green POWER-ON light shall be provided.  These indications shall be visible both on the keypad and on the VFD when the keypad is removed.

j.	A quick setup menu with factory preset typical HVAC parameters shall be provided on the VFD eliminating the need for macros.

k.	As a minimum, the following points shall be controlled and/or accessible:

- 1)	VFD Start/Stop

- 2)	Speed reference

- 3)	Fault diagnostics

- 4)	Meter points

(a)	Motor power in HP

(b)	Motor power in kW

(c)	Motor kW-hr

(d)	Motor current

(e)	Motor voltage

(f)	Hours run

(g)	Feedback signal #1

(h)	Feedback signal #2

(i)	DC link voltage

(j)	Thermal load on motor

(k)	Thermal load on VFD

(l)	Heatsink temperature

l.	Four additional Form C 230 volt programmable relays shall be available for factory or field installation within the VFD.

m.	Two set-point control interface (PID control) shall be standard in the unit.  VFD shall be able to look at two feedback signals, compare with two set-points and make various process control decisions.

n.	Floating point control interface shall be provided to increase/decrease speed in response to contact closures.

o.	Four simultaneous displays shall be available.  They shall include frequency or speed, run time, output amps and output power.  VFDs unable to show these four displays simultaneously shall provide panel meters.

p.	Sleep mode shall be provided to automatically stop the VFD when its speed drops below set “sleep” level for a specified time.  The VFD shall automatically restart when the speed command exceeds the set “wake” level.

q.	The sleep mode shall be functional in both follower mode and PID mode.

r.	Run permissive circuit shall be provided to accept a “system ready” signal to ensure that the VFD does not start until dampers or other auxiliary equipment are in the proper state for VFD operation.  The run permissive circuit shall also be capable of sending an output signal as a start command to actuate external equipment before allowing the VFD to start.

s.	The following displays shall be accessible from the control panel in actual units: Reference Signal Value in actual units, Output Frequency in Hz or percent, Output Amps, Motor HP, Motor kW, kWhr, Output Voltage, DC Bus Voltage, VFD Temperature in degrees, and Motor Speed in engineering units per application (in GPM, CFM, etc.).  VFD will read out the selected engineering unit either in a linear, square or cubed relationship to output frequency as appropriate to the unit chosen.

t.	The display shall be programmed to read in inches of water column (in-wg) for an air handler application, pressure per square inch (psi) for a pump application, and temperature (0F) for a cooling tower application.

u.	VFD shall be able to be programmed to sense the loss of load and signal a no load/broken belt warning or fault.

v.	If the temperature of the VFD’s heat sink rises to 80°C, the VFD shall automatically reduce its carrier frequency to reduce the heat sink temperature.  If the temperature of the heat sink continues to rise the VFD shall automatically reduce its output frequency to the motor. As the VFD’s heat sink temperature returns to normal, the VFD shall automatically increase the output frequency to the motor and return the carrier frequency to its normal switching speed.

w.	The VFD shall have temperature controlled cooling fans for quiet operation and minimized losses.

x.	The VFD shall store in memory the last 10 faults and related operational data.

y.	Eight programmable digital inputs shall be provided for interfacing with the systems control and safety interlock circuitry.

- Two programmable relay outputs, one Form C 240 V AC, one Form A 30 V AC, shall be provided for remote indication of VFD status.

- Three programmable analog inputs shall be provided and shall accept a direct-or-reverse acting signal.  Analog reference inputs accepted shall include two voltage (0 to 10 V DC, 2 to 10 V DC) and one current (0 to 20 mA, 4 to 20 mA) input.

- Two programmable 0 to 20 mA analog outputs shall be provided for indication of VFD status.  These outputs shall be programmable for output speed, frequency, current and power.  They shall also be programmable to provide a selected 24 V DC status indication.

- Under fire mode conditions, the VFD shall be able to be programmed to automatically default to a preset speed.

- On motors connected to variable frequency drives, 20hp or greater in size.  Provide grounding bushings to prevent archiny.

    - Interface With Building Automation System/Direct Digital Control System

a.	VFD manufacturer shall provide an interface to the BAS/DDC system.  Manufacturer shall coordinate as required with the Controls Contractor.  Provide Bacnet, Lonworks, FLN, Modbus, or any other interface required for a complete and operational system.

b.	Provide mode of operation to BAS/DDC system (hand, off, auto, etc.).  BAS/DDC graphic shall highlight or produce pop-up graphic when VFD is in hand or off.  Also, provide all points to BAS/DDC identified in section (4).K of this Specification.

    - Adjustments

a.	VFD shall have an adjustable carrier frequency in steps of not less than 0.1 kHz to allow tuning the VFD to the motor.

b.	Sixteen preset speeds shall be provided.

c.	Four acceleration and four deceleration ramps shall be provided.  Accel and decel time shall be adjustable over the range from 0 to 3,600 seconds to base speed. The shape of these curves shall be automatically contoured to ensure no-trip acceleration and deceleration.

d.	Four current limit settings shall be provided.

e.	If the VFD trips on one of the following conditions, the VFD shall be programmable for automatic or manual reset: undervoltage, overvoltage, current limit and inverter overload.

f.	The number of restart attempts shall be selectable from 0 through 20 or infinitely and the time between attempts shall be adjustable from 0 through 600 seconds.

g.	An automatic “on delay” may be selected from 0 to 120 seconds.

    - Service Conditions

a.	Ambient temperature, -10 to 40°C (14 to 104°F), without derating.

b.	0 to 95% relative humidity, non-condensing.

c.	Elevation to 3,300 feet without derating.

d.	AC line voltage variation, -10 to +10% of nominal with full output.

e.	No side clearance shall be required for cooling of any units. All power and control wiring shall be done from the bottom.

    - Quality Assurance

a.	To ensure quality and minimize infantile failures at the jobsite, the complete VFD shall be tested by the manufacturer.  The VFD shall operate a dynamometer at full load and speed and shall be cycled during the test.

b.	All optional features shall be functionally tested at the factory for proper operation.

    - Submittals

a.	Submit manufacturer’s performance data including dimensional drawings, power circuit diagrams, installation and maintenance manuals, warranty description, VFD’s FLA rating, certification agency file numbers and catalog information.

The specification lists the minimum VFD performance requirements for this project.  Each supplier shall list any exceptions to the specification.  If no departures from the specification are identified, the supplier shall be bound by the specification.

      - Harmonic filtering.  The seller shall, with the aid of the buyer’s electrical power single line diagram, providing the data required by IEEE-519, perform an analysis to initially demonstrate the supplied equipment will met the IEEE standards after installation.  If, as a result of the analysis, it is determined that additional filter equipment is required to meet the IEEE recommendations, then the cost of such equipment shall be included in the bid. A harmonic analysis shall be submitted with the approval drawings to verify compliance with the latest version of IEEE-519 voltage and current distortion limits as shown in table 10.2 and 10.3 at the point of common coupling (PCC).  The PCC shall be defined as the consumer–utility interface or primary side of the main distribution transformer.

    - Start-Up Service

a.	The manufacturer shall provide on-site start-up commissioning of the VFD and its optional circuits by a factory certified service technician who is experienced in start-up and repair services.  Sales personnel and other agents who are not factory certified shall not be acceptable as commissioning agents.  Start-up services shall include checking for verification of proper operation and installation for the VFD, its options and its interface wiring to the building automation system.  Provide start-up report to Engineer.

    - Warranty

a.	The VFD shall be warranted by the manufacturer for a period of 36 months from Substantial Completion.  The warranty shall include parts, labor, travel costs and living expenses incurred by the manufacturer to provide factory authorized on-site service.  The warranty shall be provided by the VFD manufacturer.

    - Examination

a.	Contractor to verify that job site conditions for installation meet factory recommended and code-required conditions for VFD installation prior to start-up, including clearance spacing, temperature, contamination, dust, and moisture of the environment.  Separate conduit installation of the motor wiring, power wiring, and control wiring, and installation per the manufacturer’s recommendations shall be verified.

b.	The VFD is to be covered and protected from installation dust and contamination until the environment is cleaned and ready for operation. The VFD shall not be operated while the unit is covered.

  - Hydronic Specialties

    - Manufacturers

Subject to compliance with the specified and scheduled requirements the following manufacturers will be considered, but not limited to:

Hoffman

Amtrol/Thrush

Armstrong/Aurora

Bell & Gossett

Patterson

Taco

Wheatley

    - Air Release Tank

The air release tank shall be of the in-the-pipe-line type with flanged tangential openings for inlet and outlet connections.  The inside shall be specifically designed to create a low velocity vortex for the separation of free air from the water stream.  The tank shell shall be rated at 125 PSI working pressure and shall be constructed with the ASME code for unfired pressure vessels and shall be so certified and stamped.  The tank shall be equipped with a bottom drain connection and expansion tank/vent connection.  Tank shall be line sized.  Tank shall not have a strainer.

    - Expansion Tank

The tank shall be constructed in accordance with the ASME Code for unfired pressure vessels and shall be suitable for 125 PSI water working pressure and 340ºF maximum water temperature.  The tank shall be a pre-charged, heavy duty butyl rubber diaphragm-type pressure vessel complete with standard tire charging valve.  Refer to the plans for mounting orientation.  Capacities shall be as scheduled on the drawings.

    - Suction Diffusers

Provide at the inlet of each base mounted pump, a suction diffuser as manufactured by Bell and Gossett, Victaulic, Thrush, or approved equivalent.  Each suction diffuser shall be equipped with a disposable fine mesh start-up strainer and an adjustable support foot to carry weight of inlet piping.  Victaulic Series 731 G, W731G, Bell and Gossett Suction Diffuser, or equal.

    - Triple Duty Valves

Provide at the discharge of each base mounted pump and where shown on the plans, a triple duty valve as manufactured by Bell & Gossett, Thrush  or Engineer approved equivalent.  Each valve shall perform check, shut-off and throttling functions and shall be line sized.

Alternatively, in lieu of a triple duty valve, a Victaulic grooved end “Tri-Service” valve assembly may be used in applicable piping systems.  The assembly shall consist of a Victaulic Vic-300 MasterSeal butterfly valve with memory stop feature for shut-off and balancing, and a 779 Venturi-Check for backflow prevention and flow measurement.

    - Flexible Connections

Provide at the inlet and discharge side of each base mounted pump, at each connection to major equipment requiring vibration isolation and where shown on plans, a flexible connector, Metraflex Metrasphere or Engineer approved equal.  Flexible connectors shall be of the flexible neoprene and nylon or EPDM and suitable for 225 PSI working pressure and 230°F temperature.  Couplings shall be installed per the manufacturer's recommendations, in close proximity to the source of the vibration.

Alternatively, in lieu of a flexible connector, three (3) Victaulic Style 77 flexible couplings may be used on suction side and discharge side of base mounted pumps (six Victaulic flexible couplings per pump).

    - Pressure Reducing Valve

Provide at the point of connection of the domestic water line to the hydronic system and where shown on the plans, a pressure reducing valve by Thrush, Bell and Gossett, or Engineer approved equivalent.  Such pressure reducing shall be provided with an inlet strainer and shall be set to maintain a pressure of 4 PSI in excess of that at the highest point in the hydronic system.  Each pressure reducing valves shall be line sized.

    - Vacuum Breaker

Provide, where shown on the plans, a vacuum breaker as manufactured by Huffman, Jackson or Engineer approved equivalent.

    - Manual Air Vents

Provide, where shown on the plans, at each rise in piping and where required a manual air vent.

    - Automatic Air Vents

Provide, where shown on the plans, automatic air vents.

    - Expansion Loops

Expansion loops shall be Metaflex Metra loops or Engineer approved equivalent.  Install with pipe guides and anchors as recommended by the manufacturer in all piping runs 75 feet long or greater and also where indicated on the plans.

Alternatively, in water piping systems, use adequate numbers of Victaulic Style 77 flexible couplings in header piping to accommodate thermal growth and contraction, and as required for the elimination of expansion loops.  (In accordance with Victaulic recommendations and as approved by the Engineer).  Where expansion loops are required in Victaulic piping systems, use Victaulic flexible couplings on the loop(s).

- FACTORY START-UP REPORTS

  - Provide factory start-up on site by a factory representative (not a third party contractor) for all HVAC equipment, including pumps, VFD’s, boilers, chillers, cooling towers, heat pumps, rooftop units, etc.  Submit factory start-up reports to the Engineer. The Mechanical Contractor and the Controls Contractor shall have a representative on site to correct all deficiencies noted by the factory representative.  For each deficiency noted, documentation of corrective action taken shall be submitted to Engineer.

  - At a minimum, the report submitted to the Engineer shall include the following data:

    - Water Source Heat Pumps or Water to Water Heat Pumps

      - High voltage power supply is correct and accordance with the unit nameplate.

      - The phasing of the unit is correct per the compressor rotation.

      - The field wiring and circuit protection is the correct size.

      - The low voltage control circuit wiring is correct per the unit wiring diagram.

      - The piping system is clean and complete.

      - Verify water flow is established and circulating through all units.

      - The condensate line is properly sized, run, trapped and pitched.

      - The indoor blower turns freely without rubbing.

Start-up checklist and log:  Upon unit start-up, the following items shall be checked and logged for each water source heat pump.  Note, the items listed below must be verified/checked before the system is put into full operation:

      - Entering fluid temperature (heat and cool mode)

      - Leaving fluid temperature (heat and cool mode)

      - Temperature differential (heat and cool mode)

      - Return air temperature (heat and cool mode)

      - Supply air temperature (heat and cool mode)

      - Water coil heat exchanger (water pressure “in” – psig) (heat and cool mode)

      - Water coil heat exchanger (water pressure “out” – psig) (heat and cool mode)

      - Pressure differential (psig) (heat and cool mode)

      - Compressor amps

      - Compressor volts

      - Compressor discharge line temperature (after 10 minutes)

      - Refrigerant charge (oz.)

      - Test drain pan operation

      - Check and note strainer condition.

      - Check and note filter condition.

    - Air Handling Units/Energy Recovery Units

      - Fan rotation

      - Recovery wheel rotation

      - Confirm all wiring connections are correct

      - Confirm all field wiring is correct

      - Adjust belt tensions and alignments

      - Confirm pipe connections are correct

      - Confirm sequence of operation is correct

      - Confirm damper operation

    - Base-Mounted Pumps

      - With power off, note the following:

        - pump properly secured, level, and grouted

        - pipe installed so as not to transmit stress to pump

        - coupler between pump and water shaft aligned

        - pump and motor lubricated

      - With power on, note the following:

        - impeller rotation

        - Actual amps/volts vs. nameplate amps/volts.

        - Inlet and outlet pressure

- WATER TREATMENT

  - SCOPE

Provide a one-year water treatment program for the Geothermal/Heat Pump water loop systems, including the OA-1 and baseboard heat hydronic loops.  The one-year period shall start from the date of substantial completion.  The program shall minimize corrosion, scaling, and prevent biological fouling of the piping system.

  - QUALIFICATIONS

Chemicals, service, and equipment shall be supplied by a single water treatment company for undivided responsibility.  The water treatment chemical and service supplier shall be a recognized specialist, active in the field of commercial/industrial water treatment for at least 5 years, whose major business is in the field of industrial water treatment.  The water treatment company shall have regional water analysis laboratories, service department, and full time representatives located within the trading area of the job site or facility.

Water treatment company shall be Bluegrass Kesco, Nalco, American Water Treatment, or equal.

  - SERVICE

Provide quarterly field service and Owner consultation.  System water or fluid shall be tested for proper chemical parameters, clarity, and biological activity.  If needed, provide chemical addition.  Provide any laboratory and technical assistance required to achieve a successful program.

  - CHEMICALS

Provide one year’s supply of the recommended chemical for scale and corrosion protection of the closed loop recirculating system.  If needed, provide separate chemical to control microbiological growth in the system.  Formulations shall not contain any ingredients which are harmful to system materials of construction.

  - EQUIPMENT

    - Bypass Feeder

Provide one 5 gallon bypass chemical feeder for each system.  Neptune DBF-5HP or approved equivalent.

    - HPS Loop Filter LF-1

Harmsco HIF or WB series fluid filter.  Refer to schedule on the drawings for selection.  Provide with a total of three sets of filter cartridges.

  - REPORTS

A summary of water or fluid quality and treatment shall be provided in writing to the Owner and Engineer after each quarterly site visit.  Results of quarterly biological activity tests shall also be provided to the Owner and Engineer.

- HEATING/COOLING SYSTEM CLEANING

  - GENERAL

The heating/cooling system for this contract is a hydronic heat pump system and there are several precautions which must be observed during its installation.  The Contractor is advised to read all of the manufacturer's instructions prior to commencing the installation.

  - SYSTEM START-UP

The Contractor shall include as a part of his work a hydronic system fill, flushing and purging, chemical treatment, and start-up of required equipment.  Prior to this work being completed, a flushing plan shall be submitted to the Engineer as well as signed off on by an authorized Factory Representative of the heat pump unit manufacturer.

  - CLEANING AND FLUSHING HYDRONIC HEAT PUMP PIPING SYSTEMS

    - During construction, extreme care shall be exercised to prevent all dirt and other foreign matter from entering the pipe or other parts of the system.  Pipe stored on the project shall have the open ends capped and equipment shall have all openings fully protected.  Before erection, each piece of pipe, fitting or valve shall be visually examined and all dirt removed.

    - After the system is complete it shall be thoroughly cleaned before placing in operation to rid the system of dirt, biological contamination, piping compound, loose mill scale, oil and any and all other material foreign to the water.  Coordinate flushing with Geothermal Contractor.

    - Before chemical cleaning and sterilization of the entire system, the loop field shall be flushed and purged until free of dirt, debris, and air.  During the chemical cleaning and sterilization process the supply and return run-outs shall be temporarily connected together at each heat pump location.

    - After purging of the field loop the Contractor shall add an approved system cleaning solution at the recommended concentration to the entire system.  Circulate the system with cleaner for the time recommended by the chemical manufacturer.  After prescribed circulation time, flush the system until cleaner is removed.

    - After chemical cleaning, the entire system shall be sterilized.  Introduce a solution of sodium hypochlorite to achieve a chlorine residual of 25 to 50 ppm.  Maintain this chlorine level for 12 to 24 hours.  Flush out system until chlorine residual in system equals that of the makeup water.

    - After the system has been completely cleaned and sterilized as specified herein, the individual heat pumps shall be connected permanently to the supply and return runouts and the system filled for operation under normal closed loop conditions.  Within 48 hours of the completion of the sterilization implement a water treatment program to passivate all metal surfaces.

- HVAC SYSTEM START-UP PROCEDURE

  - GENERAL

    - The goal of this procedure is for a few units to run as much as possible with the coils as cold as possible to "wring out" the water and allow it to drain away in the condensate drain pans.  Allowing all units to cycle on and off, running for short periods of time, does not dehumidify the air in the building.  Starting the system without following the steps outlined will raise the relative humidity in the building and most likely cause condensation on some of the building surfaces and HVAC system that the Contractor will be responsible to correct.

    - The high humidity and condensation occurs in buildings at start up primarily because the building is only partly occupied (or not occupied) when the HVAC system is started.  Most people believe that the answer to this problem is to turn the thermostats down very low.  The assumption is that cold air will not hold moisture.  That is not true.  What happens is that the thermostats are quickly satisfied thermally because there is very little cooling load on the building and the cooling equipment.  The terminal units then only have to run for a very short period of time to keep the thermostats satisfied and the relative humidity of the air is in fact raising. The goal is to cause the moist air to pass over coils which are cooling it and drying it without allowing more moist air to be introduced into the building.

    - To reduce the always present high humidity start-up problem, we have devised this start-up procedure that will minimize the adverse effects of the start-up.  As the building sits at start-up, all of the walls, floor, and ceilings are saturated with moisture from the air and also moisture is being released from the drying paint and curing concrete and mortar.

    - The following procedure will slowly bring down the temperature and humidity in the lightly loaded building.  It will also allow the HVAC equipment to more closely match the actual building load without students and equipment in use.

To reach these goals we require the following:

    - Set 1/3 of the units (approximately every third unit) on 74°F (no lower).  Set the other thermostats for a cooling setpoint of 90°F so the units will not cool.  Override the controls so that the fans in all units will circulate air.

    - Leave all of the interior doors open to allow the air to mix throughout the building.

    - Close all exterior windows and doors.

    - Turn off all exhaust fans and outside air units.  Outside air unit exhaust and outside air dampers shall be closed.

    - Leave all of the lights on in the building to provide a cooling load.

    - Provide portable electric heaters or dehumidifiers in any room that shows signs of condensation.

Here is a list of things you should not do:

    - Do not prop the exterior doors open during construction or while moving in furnishings.

END OF HVAC EQUIPMENT AND HYDRONIC SPECIALTIES