SECTION 202400 – IDENTIFICATIONS, TAGS, CHARTS, ETC.

- GENERAL

  - The Contractor’s attention is directed to the General and Special Conditions, General Conditions-Mechanical and to all other Contract Documents as they apply to this branch of the work.  Attention is also directed to all other Contract Documents which affect the work of this section and which are hereby made a part of the work specified herein.

- VALVE TAGS AND CHARTS

  - Standard for Lettering:

Attach Seton-Ply Discs to ceiling grid under equipment or to access doors in non-accessible ceiling.  Discs shall be applied with glue and not pinned to the grid.

| EQUIPMENT: COLOR: | ENGRAVES: |
| --- | --- |
| Valve Yellow | V. |
| Fire Damper Black | F.D. |
| Volume Damper Black | V.D. |
| Heat Pump | H.P. |

- PIPING IDENTIFICATION

  - GENERAL

    - All exposed piping installed shall be prepared for painting in finished areas (not mechanical rooms).  Exposed piping, ducts, etc shall be painted per Architectural drawings.  Provide black stenciled markers and arrows indicating direction of flow on all piping installed under this Contract after the piping has been painted.  Markers and arrows shall be painted on the piping using machine cut stencils.  All letters shall be sprayed using fast drying lacquer paint.  All markers and arrows shall be properly oriented so that descriptive name may be easily read from the floor and in exposed areas shall be arranged in a neat and orderly manner.  This shall include all piping and ducts to be labeled at the same point, every 15’, in the corridor with each label oriented in the same direction.  The contractor shall install the labels in an exposed corridor area at one location for approval prior to proceeding.   Labeling of pipe and ducts shall comply with Signage requirements of ASME A13.1.  At the Contractor’s option, Setmark or equivalent manufactured marking system may be substituted for field marking.  The following table describes the size of the color field and size of the identification letter which shall be used for pipes of different outside pipe diameters.

| OUTSIDE DIAMETER OF PIPE OR COVERING | LENGTH OF COLOR FIELD | SIZE OF LETTERS |
| --- | --- | --- |
| INCHES | INCHES | INCHES |
| 3/4 TO 1-1/4 | 8 | 1/2 |
| 1-1/2 TO 2 | 8 | 3/4 |
| 2-1/2 TO 6 | 12 | 1-1/4 |
| 8 TO 10 | 24 | 2-1/2 |
| OVER 10 | 32 | 3-1/2 |

(2)	“Concealed”, where used herein, shall mean hidden from sight as in trenches, chases, furred spaces, pipe shafts, or above hung finished hard ceilings.  “Exposed” shall mean that piping or equipment is not “concealed” as defined above.  Pipng and equipment in service tunnels, mechanical equipment rooms, storage areas, or unfinished rooms is to be considered as “exposed”.

  - PAINTING (REFER ALSO TO ARCHITECTURAL SECTION ON PAINTING)

    - Paint all equipment and metal surfaces which are not factory finished (and all damaged or rusted surfaces) in high grade rust proofing machinery enamel.  Pay particular attention to flanges, valves, unions, etc., where condensation may collect.

    - Paint exposed pipe (whether insulated or bare) and exposed surfaces (tanks, etc.).

    - All piping labels shall be a single color that is selected during the shop drawing phase.

    - Piping:

All plumbing and mechanical piping must be labeled with appropriate naming convention and color per ASME A13.1, including sprinkler lines, every 15 feet above a ceiling system and every 10 feet in an open mechanical room.

  - Water heaters, storage tanks, heat exchangers, etc., shall be painted light gray.

- EQUIPMENT IDENTIFICATION

  - All equipment shall be labeled with a lamacoid plate.  The engraving shall match the equipment tag on the construction documents.

- DUCTWORK IDENTIFICATION

  - All ductwork shall be identified as to the service of the duct and direction of flow.  The letters shall be at least two inches high and the flow arrow shall be at least six inches long.  The letters and flow arrow shall be made by precut stencils and black oil base paint with aerosol can.  Ducts located above lay-in ceilings and exposed duct shall be labeled.  Ductwork above hard ceilings is not required to be labeled.

END OF IDENTIFICATIONS