SECTION 220300 - PLUMBING EQUIPMENT

- GENERAL

  - All plumbing equipment shall comply with the latest provisions of KBC.

- WATER HEATER

  - Reheem HE, A.O. Smith or equivalent electric water heater; Refer to drawings for size and electrical requirement; copper sheathed tin coated elements (75 watt/sq. in. maximum density); glasslined tank; foam insulation; magnesium anode rod; automatic over-heat control; enamelled steel jacket; (2) elements wired for non-simultaneous operation; upper and lower thermostat; with ASME temperature and pressure relief valve; set temperature at 105°F.

- EXPANSION TANK (DOMESTIC WATER)

  - Amtrol Therm-X-Trol or equal expansion tank, precharged air chamber, stainless steel connection and heavy duty butyl diaphragm.  Refer to plans for model number and size.

- RECIRCULATING DOMESTIC HOT WATER PUMPS

  - Thrush, Armstrong, Bell and Gossett or approved equivalent all bronze in-line centrifugal circulating pump with mechanical seals, drip proof motor and all required overloads, starters and disconnects.

END OF PLUMBING EQUIPMENT