SECTION 230100 - PUMPS

- GENERAL

  - The Contractor's attention is directed to the General and Special Conditions, General Provisions - Mechanical and to all other contract Documents as they apply to this branch of the work.  Attention is also directed to other sections of the specifications which affect the work of this section and which are hereby made a part of the work specified herein.

  - All required motor starters shall be furnished with the respective pump.

  - Electric motors shall be furnished with the pumps and shall be of the size and type scheduled or otherwise specified.  All motors shall be UL labeled and shall comply with applicable NEMA standard.

  - Shop drawings shall be submitted as required by Section 200300 and shall include complete pump specifications, installation and start-up instructions, current and accurate pump performance curves with the selection points clearly indicated, maintenance data and spare parts lists.

  - Pumps shall be factory tested, cleaned and painted prior to shipment.  Size, type, capacity and electrical characteristics are listed in the pump schedule.

  - Insofar as possible, all pumps shall be by the same manufacturer.

  - Pump shall have data plate indicating horsepower, voltage, phase, ampacity, pressure head, and flow rate.

  - Special notes for pumps controlled by variable frequency drives:

    - Supplier shall provide the largest non-overloading impeller size for the specified pump motor horsepower, regardless of the specified pump head given on the pump schedule(s).

    - Pumps less than 100 HP in size shall be furnished with shaft grounding kit, Aegis SGR Bearing Protection Ring or equal.  One shaft grounding ring and related hardware shall be provided on drive end or non-drive end of motor per manufacturer’s instructions.  Ground motor frame per manufacturer’s instructions.  Install kit in strict accordance with manufacturer’s instructions.

    - The contractor shall include in their Submittal the variable speed performance for each pump that shall be operated with a variable frequency drive.

- MATERIAL

  - BASE MOUNTED PUMPS

    - Type:  Horizontal, base mounted, end suction, single stage, flexible coupled, 175 PSI working pressure.

    - Pump Body: Cast iron, flanged gauge and drain tappings, bronze fitted.

    - Shaft:  Stainless steel.  Refer to special notes for pumps controlled by VFD’s above for shaft grounding kit specification.

    - Bearing:  Re-lubricatable ball bearing.

    - Seal:  Mechanical, carbon ring with ceramic seal.

    - Motor:  open, drip proof, re-lubricatable ball bearing. Minimum efficiency per NEMA Premium Induction Motor Efficiency.

    - Impeller:  Enclosed, balanced.

    - Base:  Structural steel.

    - Coupling:  Flexible with coupling guard.

    - Manufacturers: Subject to compliance with the specified and scheduled requirements.  Pumps by the following manufacturers will be considered:

Amtrol/Thrush

Armstrong/Aurora

Bell and Gossett

Federal Pump

Patterson

Sigmund

Grundfos

Taco

    - SELECTIONS:

Refer to the schedule on the plans for base-mounted pump selections.

END OF PUMPS