## LEED Scorecard
12 | 1 | 13 | Sustainable Sites |  |  | Possible Points: 26 | Responsible Party | Notes | Compliance Option Chosen | Questions
Y | N | ?
Y |  |  | Prereq 1 | Construction Activity Pollution Prevention |  | Required | VLA | Document
1 |  |  | Credit 1 | Site Selection |  | 1 | VLA | Verify intent of credit is met
|  | 5 | Credit 2 | Development Density and Community Connectivity |  | 5 | VLA | Verify that site does not comply with density
| 1 |  | Credit 3 | Brownfield Redevelopment |  | 1 | NKU/VLA | Verify that site is not a brownfield
6 |  |  | Credit 4.1 | Alternative Transportation - Public Transportation Access |  | 6 | VLA | Verify www.tankbusroute.org 1/4 mile of 2 bus lines (Route 11 & 25)
1 |  |  | Credit 4.2 | Alternative Transportation - Bicycle Storage & Changing Rooms |  | 1 | Omni | We will have enough showers, need to add bike racks for 5% of FTE.
|  | 3 | Credit 4.3 | Alternative Transportation - Low-Emitting and Fuel-Efficient Vehicles |  | 3 | NKU/VLA | Dedicated Spaces consult with Owner
|  | 2 | Credit 4.4 | Alternative Transportation - Parking Capacity |  | 2 | NKU/VLA | Do not exceed local zoning requirements AND provide 5% preferred carpool spots.
|  | 1 | Credit 5.1 | Site Development - Protect Or Restore Habitat |  | 1 | VLA | Requires restoration of 50% of site (not available due to artificial turf ?)
|  | 1 | Credit 5.2 | Site Development - Maximize Open Space |  | 1 | VLA | Exceed P&Z requirements by 25% open "green" space
1 |  |  | *Credit 6.1 | Stormwater Design - Quantity Control |  | 1 | VLA | Calculate: 25% decrease in 2-year, 24-hour design storm.
1 |  |  | Credit 6.2 | Stormwater Design - Quality Control |  | 1 | NKU/VLA | Capturing & Treating rainwater: Target Zero runoff
1 |  |  | *Credit 7.1 | Heat Island Effect - Non-roof |  | 1 | VLA | 50% of hardscape needs to be: 1) shaded, 2) SRI of 29+, 3) 50% pervious.
1 |  |  | Credit 7.2 | Heat Island Effect - Roof |  | 1 | NKU/Omni | >2:12 need SRI of 29, <=2:12 need SRI of 78/ Depends on re-roof of Albright
|  | 1 | Credit 8 | Light Pollution Reduction |  | 1 | NKU/CMTA | Interior: Can we meet the hour requirements for light shutoff from 11PM - 5AM. Exterior lighting needs photometric. Security Walkways issue…Verify Campus Standards…Very difficult credit.
6 | 1 | 3 | Water Efficiency |  |  | Possible Points: 10 | Responsible Party | Notes | Compliance Option Chosen | Questions
Y | N | ?
Y |  |  | Prereq 1 | Water Use Reduction - 20% Reduction |  | Required | CMTA/Counsilman-Hunsaker | Confirm role of Pool
2 |  | 2 | Credit 1 | Water Efficient Landscaping |  | 2 to 4 | NKU/VLA | Confirm NKU policy on 50% reduction: Plant Material/irrigation efficiency/capture rainwater/etc.
|  |  |  | 2 | Reduce by 50% | 2 |  | Confirm that water for artificial turf is not considered irrigation
|  |  |  | 4 | No Potable Water Use or Irrigation | 4 |  | Confirm NKU policy on irrigation.
2 |  |  | Credit 2 | Innovative Wastewater Technologies |  | 2 | CMTA | Awaiting CMTA Comment
2 | 1 | 1 | Credit 3 | Water Use Reduction |  | 2 to 4 | CMTA | May not be able to go to 35% ?? Showers/Pool
|  |  |  | 2 | Reduce by 30% | 2
|  |  |  | N | Reduce by 35% | 3
|  |  |  | N | Reduce by 40% | 4
9 | 17 | 9 | Energy and Atmosphere |  |  | Possible Points: 35 | Responsible Party | Notes | Compliance Option Chosen | Questions
Y | N | ?
Y |  |  | Prereq 1 | Fundamental Commissioning of Building Energy Systems |  | Required | NKU TBA | Need to hire CxA
Y |  |  | Prereq 2 | Minimum Energy Performance |  | Required | CMTA | 10% improvement over ASHRAE 90.1-2007 baseline.
Y |  |  | Prereq 3 | Fundamental Refrigerant Management |  | Required | CMTA | Required by building code. Need to retrofit the existing Seresco Pool AHU with R-407C (currently R-22)
7 | 9 | 3 | *Credit 1 | Optimize Energy Performance |  | 1 to 19 | CMTA | We'll see what lighting, HVAC, and envelope improvements can obtain. 3 point penalty for using Campus Steam/Chilled. Geothermal well field helps!
|  |  |  | 1 | Improve by 12% for New Buildings or 8% for Existing Buildings | 1 |  | HB 2: 7 Credits required.
|  |  |  | 1 | Improve by 14% for New Buildings or 10% for Existing Buildings | 2
|  |  |  | 1 | Improve by 16% for New Buildings or 12% for Existing Buildings | 3
|  |  |  | 1 | Improve by 18% for New Buildings or 14% for Existing Buildings | 4
|  |  |  | 1 | Improve by 20% for New Buildings or 16% for Existing Buildings | 5
|  |  |  | 1 | Improve by 22% for New Buildings or 18% for Existing Buildings | 6
|  |  |  | 1 | Improve by 24% for New Buildings or 20% for Existing Buildings | 7 | CMTA/Omni | Can we exceed 24%??
|  |  |  | ? | Improve by 26% for New Buildings or 22% for Existing Buildings | 8
|  |  |  | ? | Improve by 28% for New Buildings or 24% for Existing Buildings | 9
|  |  |  | ? | Improve by 30% for New Buildings or 26% for Existing Buildings | 10
|  |  |  | X | Improve by 32% for New Buildings or 28% for Existing Buildings | 11
|  |  |  | X | Improve by 34% for New Buildings or 30% for Existing Buildings | 12
|  |  |  | X | Improve by 36% for New Buildings or 32% for Existing Buildings | 13
|  |  |  | X | Improve by 38% for New Buildings or 34% for Existing Buildings | 14
|  |  |  | X | Improve by 40% for New Buildings or 36% for Existing Buildings | 15
|  |  |  | X | Improve by 42% for New Buildings or 38% for Existing Buildings | 16
|  |  |  | X | Improve by 44% for New Buildings or 40% for Existing Buildings | 17
|  |  |  | X | Improve by 46% for New Buildings or 42% for Existing Buildings | 18
|  |  |  | X | Improve by 48+% for New Buildings or 44+% for Existing Buildings | 19
| 6 | 1 | *Credit 2 | On-Site Renewable Energy |  | 1 to 7 | CMTA | Estimate Cost of PV for 1% of total building energy consumption (including process consumption). This will actually give us 2 points: the credit plus the regional achievement. Need grant.
|  |  |  | ? | 1% Renewable Energy | 1
|  |  |  | N | 3% Renewable Energy | 2
|  |  |  | N | 5% Renewable Energy | 3
|  |  |  | N | 7% Renewable Energy | 4
|  |  |  | N | 9% Renewable Energy | 5
|  |  |  | N | 11% Renewable Energy | 6
|  |  |  | N | 13% Renewable Energy | 7
2 |  |  | Credit 3 | Enhanced Commissioning |  | 2 | NKU TBA | NKU will need to procure CxA and have review of DD Phase prior to CD Phase
|  | 2 | Credit 4 | Enhanced Refrigerant Measurement |  | 2 | CMTA | Need to investigate central plant refrigerant impact on the average refrigerant atmospheric impact
|  | 3 | Credit 5 | Measurement and Verification |  | 3 | CMTA/CxA/NKU | We will add capabilities. Need to work with NKU on monitoring strategies.
| 2 |  | *Credit 6 | Green Power |  | 2 | CMTA/NKU | This is something we can pursue after the fact. We'll need to make sure that the green power quantity we need is available through Duke Energy
7 | 1 | 6 | Materials and Resources |  |  | Possible Points: 14 | Responsible Party | Notes | Compliance Option Chosen | Questions
Y | N | ?
Y |  |  | Prereq 1 | Storage and Collection of Recyclables |  | Required | Cannon Design | Program & Design Issue: Need 500 NSF of dedicated room
1 | 1 | 1 | Credit 1.1 | Building Reuse - Maintain Existing Walls, Floors, and Roof |  | 1 to 3 | Omni | Will need to do calculation on impact of exterior wall removal and track removal
|  |  |  | 1 | Reuse 55% | 1
|  |  |  | ? | Reuse 75% | 2
|  |  |  | N | Reuse 95% | 3
1 |  |  | Credit 1.2 | Building Reuse - Maintain 50% of Interior Non-Structural Elements |  | 1 | Omni | Will need to calculate what is retained on level 2 & 3. Need to minimize Locker Room Renovations
2 |  |  | Credit 2 | Construction Waste Management |  | 1 to 2 | Construction Manager | Plan will be developed in Construction Phase
|  |  |  | 1 | 50% Recycled or Salvaged | 1
|  |  |  | 1 | 75% Recycled or Salvaged | 2
|  | 2 | Credit 3 | Materials Reuse |  | 1 to 2 | Omni/NKU | Challenging to meet 5%
|  |  |  | ? | Reuse 5% | 1
|  |  |  | ? | Reuse 10% | 2
2 |  |  | Credit 4 | Recycled Content |  | 1 to 2 | Omni/bfmj/CM | Structural Steel, Gypsum Board, metal panles,
|  |  |  | 1 | 10% of Content | 1
|  |  |  | 1 | 20% of Content | 2
|  | 2 | Credit 5 | Regional Materials |  | 1 to 2 | Omni | We'll need to check extracted AND manufactured options
|  |  |  | ? | 10% of Materials | 1
|  |  |  | ? | 20% of Materials | 2
|  | 1 | Credit 6 | Rapidly Renewable Materials |  | 1 | CANNON / Omni | Confirm Opportunities/ Bamboo Gym Floors?
1 |  |  | *Credit 7 | Certified Wood |  | 1 | CANNON / Omni | Maybe for built in cabinetry/ Doors/ miscl rough carpentry/Maple Gym Floors
8 | 3 | 4 | Indoor Environmental Quality |  |  | Possible Points: 15 | Responsible Party | Notes | Compliance Option Chosen | Questions
Y | N | ?
Y |  |  | Prereq 1 | Minimum Indoor Air Quality Performance |  | Required | CMTA | Spec
Y |  |  | Prereq 2 | Environmental Tobacco Smoke (ETS) Control |  | Required | Omni/NKU | Spec / This will include No Smoking 25 ft. outside of bldg too.
1 |  |  | Credit 1 | Outdoor Air Delivery Monitoring |  | 1 | CMTA/Omni | Will put into design
| 1 |  | Credit 2 | Increased Ventilation |  | 1 | CMTA | Energy Consumption goes up.
1 |  |  | Credit 3.1 | Construction IAQ Management Plan - During Construction |  | 1 | CM / CMTA | CM and CxA will implement
|  | 1 | Credit 3.2 | Construction IAQ Management Plan - Before Occupancy |  | 1 | CM / CMTA | This is an expensive credit.
1 |  |  | Credit 4.1 | Low-Emitting Materials - Adhesives and Sealants |  | 1 | Omni | Will put into design
1 |  |  | Credit 4.2 | Low-Emitting Materials - Paints and Coverings |  | 1 | Omni | Will put into design
1 |  |  | Credit 4.3 | Low-Emitting Materials - Flooring Systems |  | 1 | Omni | Will put into design
1 |  |  | Credit 4.4 | Low-Emitting Materials - Composite Wood and Agrifiber Products |  | 1 | Omni | Will put into design
1 |  |  | Credit 5 | Indoor Chemical and Pollutant Source Control |  | 1 | CMTA / Omni | Spec
|  | 1 | Credit 6.1 | Controllability of Systems - Lighting |  | 1 | CMTA / NKU | Requires Individual controls (NKU Isuue)
|  | 1 | Credit 6.2 | Controllability of Systems - Thermal Comfort |  | 1 | CMTA / NKU | Requires individual controls (NKU Issue)
1 |  |  | Credit 7.1 | Thermal Comfort - Design |  | 1 | Omni/CMTA | Discussion / Must Meet ASHRAE 55-2004
|  | 1 | Credit 7.2 | Thermal Comfort - Verification |  | 1 | Omni/CMTA/NKU | Requires Owner Survey 6-18 months after occupancy
| 1 |  | *Credit 8.1 | Daylight and Views - Daylight |  | 1 | Omni/CMTA | We need 75% of Regularly Occupied Spaces to be lit by daylight (Offices do not conform)
| 1 |  | Credit 8.2 | Daylight and Views - Views |  | 1 | Omni | Line of Sight 75%/90% for building occupants (Offices layout does not conform)
3 | 1 | 2 | Innovation and Design Process |  |  | Possible Points: 6 | Responsible Party | Notes | Compliance Option Chosen | Questions
Y | N | ?
1 |  |  | Credit 1.1 | Innovation in Design: Building as Teaching Tool |  |  | Omni/NKU/CMTA | This should be something we create based on NKU's building tour plans. May need additional signage to enhance education. Energy Dashboard. Will need to develop.
1 |  |  | Credit 1.2 | Innovation in Design: Green Housekeeping |  |  | NKU | This is a potential. Was Considered on Griffin Hall. Needs NKU buy-in
| 1 |  | Credit 1.3 | Innovation in Design: TBA
|  | 1 | Credit 1.4 | Innovation in Design: Exemplary Performance - Landfill Diversion |  |  | NKU Cost issue | If we divert 90% of construction materials, we can get exemplary performance.
|  | 1 | Credit 1.5 | Innovation in Design: Exemplary Performance - Recycled Content |  |  | NKU Cost Issue | If we use 30% of our materials with recycled content, we can get this credit.
1 |  |  | Credit 2 | LEED Accredited Professional |  |  | Omni | Michael Jacobs is LEED AP
2 | 0 | 3 | Regional Priority Credits - Limit 4 of 6 Possible |  |  | Possible Points: 4 | Responsible Party | Notes | Compliance Option Chosen | Questions
Y | N | ? |  |  | Zip Code 41099 Highland Heights, KY |  |  | Zip Code 41099
1 |  |  | Credit 1.x | Regional Priority: Must Meet IEQc7.1 |  |  | CMTA | Thermal Comfort. Must meet ASHRAE 55-2004
1 |  |  | Credit 1.x | Regional Priority: Must Meet SS c6.1 |  |  | VLA | Storm Water Design if we get SS 6.1
|  | 1 | Credit 1.x | Regional Priority: WE c3 (40%) |  |  | CMTA | 40% Water Use Reduction is challenging with Showers
|  | 1 | Credit 1.x | Regional Priority: EA c1 (28%/24%) |  |  | CMTA | Optimize Energy Performance 2 Points higher than target
|  | 1 | Credit 1.x | Regional Priority: EAc2 (1%) Possible with Solar PV Grant |  |  | CMTA | On Site Renewable Energy would require Grant
Credit 1.x
47 | 24 | 40 | TOTAL |  |  | Possible Points: 110
Certified: 40 - 49 Points
|  |  | Silver: 50 - 59 Points |  | Target +55 Points
Gold: 60 - 79 Points
Platinum: 80 -110 Points
Note on D4: To reduce pollution from construction activities by controlling soil erosion, waterway sedimentation and airborne dust generation.
Note on D5: To avoid development of inappropriate sites and reduce the environmental impact from the location of a building on a site.
Note on D6: To channel development to urban areas with existing infrastructure, protect green fields and preserve habitat and natural resources.
Note on D7: To rehabilitate damaged sites where development is complicated by environmental contamination and to reduce pressure on undeveloped land.
Note on D8: To reduce pollution and land development impacts from automobile use.
Note on D9: To reduce pollution and land development impacts from automobile use.
Note on D10: To reduce pollution and land development impacts from automobile use.
Note on D11: To reduce pollution and land development impacts from automobile use.
Note on D12: To conserve existing natural areas and restore damaged areas to provide habitat and promote biodiversity.
Note on D13: To promote biodiversity by providing a high ratio of open space to development footprint.
Note on D14: To limit disruption of natural hydrology by reducing impervious cover, increasing on-site infiltration, reducing or eliminating pollution from stormwater runoff and eliminating contaminants.
Note on D15: To limit disruption and pollution of natural water flows by managing stormwater runoff.
Note on D16: To reduce heat islands to minimize impacts on microclimates and human and wildlife habitats.
Note on D17: To reduce heat islands to minimize impacts on microclimates and human and wildlife habitats.
Note on D18: To minimize light trespass from the building and site, reduce sky-glow to increase night sky access, improve nighttime visibility through glare reduction and reduce development impact from lighting on nocturnal environments.
Note on D22: To increase water efficiency within buildings to reduce the burden on municipal water supply and wastewater systems.
Note on D23: To limit or eliminate the use of potable water or other natural surface or subsurface water resources available on or near the project site for landscape irrigation.
Note on D26: To reduce wastewater generation and potable water demand while increasing the local aquifer recharge.
Note on D27: To further increase water efficiency within buildings to reduce the burden on municipal water supply and wastewater systems.
Note on D34: To verify that energy related systems are installed, calibrated, and perform according to the OPR, BoD, and CD's.
Note on D35: To establish the minimum level of energy efficiency for the proposed building and systems to reduce environmental and economic impacts associated with excessive energy use.
Note on D36: To reduce stratospheric ozone depletion.
Note on D37: To achieve increasing levels of energy performance beyond the prereq standard to reduce environmental and economic impacts associated with excessive energy use.
Note on D57: : To encourage and recognize increasing levels of on-site renewable energy self-supply to reduce environmental and economic impacts associated with fossil fuel energy use.
Note on D65: To begin the commissioning process early in the design process and execute additional activities after systems performance verification is completed.
Note on D66: To reduce ozone depletion and support early compliance with the Montreal Protocol while minimizing direct contributions to climate change.
Note on D67: To provide for the ongoing accountability of building energy consumption over time.
Note on D68: To encourage the development and use of grid-source, renewable energy technologies on a net zero pollution base.
Note on D72: To facilitate the reduction of waste generated by building occupants that is hauled to and disposed of in landfills.
Note on D73: To extend the life cycle of existing building stock, conserve resources, retain cultural resources, reduce waste and reduce environmental impacts of new buildings as they relate to materials manufacturing and transport.
Note on D77: To extend the life cycle of existing building stock, conserve resources, retain cultural resources, reduce waste and reduce environmental impacts of new buildings as they relate to materials manufacturing and transport.
Note on D78: To divert construction and demolition debris from disposal in landfills and incineration facilities. Redirect recyclable recovered resources back to the manufacturing process and reusable materials to appropriate sites.
Note on D81: To reuse building materials and products to reduce demand for virgin materials and reduce waste, thereby lessening impacts associated with the extraction and processing of virgin resources.
Note on D84: To increase demand for building products that incorporate recycled content materials, thereby reducing impacts resulting from extraction and processing of virgin materials.
Note on D87: To increase demand for building materials and products that are extracted and manufactured within the region, thereby supporting the use of indigenous resources and reducing environmental impacts resulting from transportation.
Note on D90: To reduce the use and depletion of finite raw materials and long-cycle renewable materials by replacing them with rapidly renewable materials.
Note on D91: To encourage environmentally responsible forest management.
Note on D95: To establish minimum indoor air quality performance to enhance IAQ in buildings, thus contributing to the comfort and well-being of the occupants.
Note on D96: To prevent or minimize exposure of building occupants, indoor surfaces, and ventilation air distribution system to environmental tobacco smoke.
Note on D97: To provide capacity for ventilation system monitoring to help promote occupant comfort and well-being.
Note on D98: To provide additional outdoor air ventilation to improve IAQ and promote occupant comfort, well-being, and productivity.
Note on D99: To reduce IAQ problems resulting from constructability or renovation and promote the comfort and well-being of construction workers and building occupants.
Note on D100: To reduce IAQ problems resulting from construction or renovation and promote the comfort and well-being of construction workers and building occupants.
Note on D101: To reduce the quantity of indoor air contaminants that are odorous, irritating, and/or harmful to the comfort and well-being of installers and occupants.
Note on D102: To reduce the quantity of indoor air contaminants that are odorous, irritating, and/or harmful to the comfort and well-being of installers and occupants.
Note on D103: To reduce the quantity of indoor air contaminants that are odorous, irritating, and/or harmful to the comfort and well-being of installers and occupants.
Note on D104: To reduce the quantity of indoor air contaminants that are odorous, irritating, and/or harmful to the comfort and well-being of installers and occupants.
Note on D105: To minimize building occupant exposure to potentially hazardous particulates and chemical pollutants.
Note on D106: To provide high level of lighting system control by individual occupants or groups in multi-occupant spaces and promote their productivity, comfort, and well-being.
Note on D107: To provide high level of thermal comfort system control by individual occupants or groups in multi-occupant spaces and promote their productivity, comfort, and well-being. (air temp, radiant temp, air speed, or humidity)
Note on D108: To provide a comfortable thermal environment that promotes occupant productivity and well-being.
Note on D109: To provide for the assessment of building occupants' thermal comfort over time.
Note on D110: To provide for the building occupants with a connection between indoor spaces and the outdoors through the introduction of daylight and views into the regularly occupied areas of the building.
Note on D111: To provide for the building occupants with a connection between indoor spaces and the outdoors through the introduction of daylight and views into the regularly occupied areas of the building.
Note on D114: : To provide design teams and projects the opportunity to achieve exceptional performance above the requirements set by LEED and/or innovative performance in Green Building categories not specifically addressed by the LEED system.

## Ledger1
Date | Posted Date | Description | Category | Debit | Credit | Balance

## Ledger1 (2)
Date | Check # | Payee | Category | Debit | Credit | Balance

## Ledger1 (3)
Pri | Date | Check # | Payee | Category | Memo | Posted | Debit | Credit | Balance
n

## Ledger1 (4)
Priority | Mailed | Check # | Invoice | Due Date | Date Paid | Posted | Category | Payee | Customer | Memo | Debit | Credit | Balance
n

## Ledger1 (5)
Date | Payee | Debit | Credit | Balance